Technical Glass Products has included notes in this specification to assist you in tailoring the content to your project.  These comments will appear on your screen in blue.  To hide them and view only the specification, do the following:  Click on “Tools” on your Microsoft Word toolbar.  Under Tools, select “Options.” On the “View” tab, under “Formatting Marks,” remove the check mark from the “Hidden Text” box.  Then click “OK.”  All blue text will then be hidden.  For assistance, call Technical Glass Products at 1-800-426-0279.

This guide specification is a supplier-specific proprietary product specification using the proprietary method of specifying applicable to project specifications and master guide specifications. Optional text is indicated by brackets []; delete optional text in final copy of specification.

This Section specifies the “FireLite®” fire–rated glass ceramic (not an high impact safety-rated glass) supplied by Technical Glass Products further described in Part 2 – Products. Compatible with Fireframes Designer Series frames supplied by Technical Glass Products.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

SECTION 08817 - FIRE-RATED GLASS - firelite

- GENERAL

      - SUMMARY

        - Section Includes:

          - Fire-rated glazing materials installed as [transoms] [borrowed lites] [windows] in fire-rated frames.

Verify that Section titles referenced below are correct for this Project's Specifications; Section titles may have changed. Revise Section number and title below to suit project requirements, specification practices and section content. Refer to CSI MasterFormat for other section numbers and titles.

        - Related Sections include the following:

          - Section 06400 “Architectural Woodwork” for wood frames for doors, sidelights, transoms, borrowed lights.

          - Section 08110 “Steel Doors and Frames” for vision panels in interior doors and interior vision panel (borrowed lites) frames.

          - Section 08210 “Flush Wood Doors” for vision panels in interior doors.

          - Section 08112 “Stile and Rail Wood Doors” for vision panels in interior doors.

          - Section 08510 “Steel Windows”.

      - references

Adjust lists below to suit Project.

        - American Society for Testing and Materials (ASTM):

          - ASTM E2010-01:  Standard Test Method for Positive Pressure Fire Tests of Window Assemblies.

        - Glass Association of North America (GANA):

          - GANA – Glazing Manual.

          - FGMA – Sealant Manual.

        - National Fire Protection Association (NFPA):

          - NFPA 80:  Fire Doors and Windows.

          - NFPA 257 – Fire Tests of Window Assemblies.

        - Underwriters Laboratories, Inc. (UL):

          - UL 9 – Fire Tests of Window Assemblies.

Following are Canadian Standards

        - Standard Council of Canada:

          - ULC Standard CAN4-S106: Fire Tests of Window Assemblies.

        - <Insert building code name used by authority having jurisdiction>.

      - PERFORMANCE REQUIREMENTS

        - Fire-rated glass ceramic clear and wireless glazing material listed for use in non-impact safety-rated locations such as transoms and borrowed lites with fire rating requirements ranging from 20 to 90 minutes with hose stream test.

        - Passes positive pressure test standards UBC 7-2 and UBC 7-4.

- Note:  This product is not a barrier to radiant heat. This product does not meet test standards ASTM E 119 or UL 263. If your jurisdiction requires a “barrier to heat” product, please contact Technical Glass Products regarding Pyrostop.

- FireLite is not an impact safety-rated product and should not be specified as such.

- FireLite side may be lightly sandblasted or etched without affecting the fire rating.

      - SUBMITTALS

- Note:  Specify submittal requirements for fire-rated doors and fire-rated frames, including glass stops in the appropriate Sections.

        - Comply with requirements of Section <Insert Section #>.

        - Product data:  Submit manufacturer’s technical data for each glazing material required, including installation and maintenance instructions.

        - Certificates of compliance from glass and glazing materials manufacturers attesting that glass and glazing materials furnished for project comply with requirements. Separate certification will not be required for glazing materials bearing manufacturer’s permanent label designating type and thickness of glass, provided labels represent a quality control program involving a recognized certification agency or independent testing laboratory acceptable to authority having jurisdiction.

        - Product Test Listings:  From UL indicating fire-rated glass complies with requirements, based on comprehensive testing of current product.

        - Samples:  Submit, for verification purposes, approx. 8-inch by 10-inch sample for each type of glass indicated.

      - QUALITY ASSURANCE

        - Glazing Standards:  GAMA Glazing Manual and FGMA Sealant Manual.

        - Fire Protective Rated Glass:  Each lite shall bear permanent, nonremovable label of UL certifying it for use in tested and rated fire protective assemblies.

      - delivery, storage, and handling

        - Deliver, store, and handle materials under provisions of Section <Insert Section #>.

        - Deliver materials to specified destination in manufacturer’s or distributor’s packaging, undamaged, complete with installation instructions.

        - Store off ground, under cover, protected from weather and construction activities.

      - WARRANTY

        - Provide manufacturer's limited warranty under provision of Section <Insert Section #>.

- PRODUCTS

      - Fire-Rated Glazing Materials

        - Manufacturer: FireLite® as manufactured by Nippon Electric Glass Company, Ltd., and distributed by Technical Glass Products, Kirkland, Washington, voice 1-800-426-0279, fax 1-800-451-9857, e-mail sales@fireglass.com, web site www.fireglass.com.

        - Properties:

- Note:  Figures are for Premium (polished) FireLite. Figures will differ slightly for Standard (unpolished) and Obscure (patterned) surface finishes.

          - Thickness:  3/16 inch [5 mm].

          - Weight:  2.4 lbs./sq. ft.

          - Approximate Visible Transmission:  88 percent.

          - Approximate Visible Reflection:  9 percent.

          - Hardness (Vicker’s Scale):  700.

          - Fire-rating:  20 minutes to 90 minutes.

          - Impact Safety Resistance:  None.

          - Positive Pressure Test:  UL 10C, UBC 7-2 and 7-4; passes.

          - Surface Finish:  Premium (polished) [Standard (unpolished)] [Obscure (patterned)].

        - Maximum sheet sizes based on surface finish:

          - Premium:  48 inches by 96 inches.

          - Standard:  48 inches by 96 inches.

          - Obscure:  36 inches by 96 inches.

        - Labeling:  Permanently label each piece of FireLite with the FireLite® logo, UL logo and fire rating in sizes up to 3,325 sq. in., and with the FireLite® label only for sizes that exceed the listing (as approved by the local authority having jurisdiction).

        - Fire Rating:  Fire rating listed and labeled by UL for fire rating scheduled at opening locations on drawings, when tested in accordance with [ASTM E2074-00 and ASTM E2010-01] [ULC Standards CAN4 S-104 and CAN4 S-106] [NFPA 257] [UL 9 and UL 10B].

        - Substitutions:  No substitutions permitted.

      - GLAZING COMPOUND FOR FIRE-RATED GLAZiNG MATERIALS

- Note:  Select one the following: glazing tape, glazing compound or silicone sealant.

        - Glazing Tape:  Closed cell polyvinyl chloride (PVC) foam, coiled on release paper over adhesive on two sides, maximum water absorption by volume of 2 percent. Glass panels that exceed 1,393 sq. inches for 90-minute ratings must be glazed with fire-rated glazing tape supplied by manufacturer.

        - [Glazing Compound: DAP 33 putty.]

        - [Silicone Sealant:  One-part neutral curing silicone, medium modulus sealant, Type S; Grade NS; Class 25 with additional movement capability of 50 percent in both extension and compression (total 100 percent); Use (Exposure) NT; Uses (Substrates) G, A, and O as applicable. Available Products:

          - Dow Corning 795 - Dow Corning Corp.

          - Silglaze-II 2800 - General Electric Co.

          - Spectrem 2 - Tremco Inc.

        - Setting Blocks:  Neoprene, EPDM, or silicone; tested for compatibility with glazing compound; of 70 to 90 Shore A hardness.

        - Cleaners, Primers, and Sealers:  Type recommended by manufacturer of glass and gaskets.

      - FABRICATION

        - Fabricate glass and other glazing products in sizes required to glaze openings indicated for Project, with edge and face clearances, edge and surface conditions, and bite complying with recommendations of product manufacturer and referenced glazing standard as required to comply with system performance requirements.

- EXECUTION

      - EXAMINATION

        - Examine glass framing, with glazier present, for compliance with the following:

          - Manufacturing and installation tolerances, including those for size, squareness, offsets at corners.

          - Minimum required face or edge clearances.

          - Observable edge damage or face imperfections.

        - Do not proceed with glazing until unsatisfactory conditions have been corrected.

        - Clean glazing channels and other framing members receiving glass immediately before glazing.  Remove coatings that are not firmly bonded to substrates.

      - INSTALLATION (GLAZING)

        - Comply with referenced FGMA standards and instructions of manufacturers of glass, glazing sealants, and glazing compounds.

        - Protect glass from edge damage during handling and installation.  Inspect glass during installation and discard pieces with edge damage that could affect glass performance.

        - Set units of glass in each series with uniformity of pattern, draw, bow, and similar characteristics.

        - Cut glazing tape to length and set against permanent stops, flush with sight lines to fit openings exactly, with stretch allowance during installation.

        - Place setting blocks located at quarter points of glass with edge block no more than 6 inches from corners.

        - Glaze vertically into labeled fire-rated metal frames or partition walls with same fire rating as glass and push against tape for full contact at perimeter of pane or unit.

        - Place glazing tape on free perimeter of glazing in same manner described above.

        - Install removable stop and secure without displacement of tape.

        - [Use specified glazing compound, without adulteration; bed glazing material in glazing compound; entirely fill all recess and spaces. Provide visible glazing compound with smooth and straight edges.]

        - Install so that appropriate [UL] [FireLite®] markings remain permanently visible.

      - PROTECTION AND CLEANING

        - Protect glass from contact with contaminating substances resulting from construction operations.  Remove any such substances by method approved by glass manufacturer.

        - Wash glass on both faces not more than four days prior to date scheduled for inspections intended to establish date of substantial completion.  Wash glass by method recommended by glass manufacturer.

      - GLAZING SCHEDULE

| Rating | Assembly | Max. Exposed Area (Sq. In.) | Max. Width Of Exposed Glazing (In.) | OR | Max. Height Of Exposed Glazing (In.) | Stop Height |
| --- | --- | --- | --- | --- | --- | --- |
| 20 to 60 min. 90 min. | Other than doors HMS or wood* Fireframes D.S. Other than doors HMS Fireframes D.S. | 3,325 3,325 2,627 2,627 | 95 95 56 ½” 56 ½” |  | 95 95 56 ½” 56 ½” | 5/8” 3/4" 5/8” 3/4" |

- *  HMS indicates hollow metal steel framing.  Fireframes D.S. indicates Designer Series narrow profile framing available from TGP.  For wood frames, check with manufacturer for maximum tested glass sizes.

Note:  Individual lite sizes cannot exceed maximum exposed area shown above.

Note:  Special approval is required from the local authority having jurisdiction when using FireLite® in applications requiring a non-standard rating or sizes larger than those scheduled above and in paragraph 2.1, C. In such cases FireLite® will be furnished with a FireLite® label only.

END OF SECTION