Armstrong World Industries

Ceiling & Suspension Systems Specification

| Job Number: |  | E-mail Address: |  |
| --- | --- | --- | --- |
| Job Type: |  | Zip Code: |  |
| Project Name: |  | Date & Time: |  |
| Firm Name: |  | Rep Name: |  |
| Contact Name: |  | Rep Phone: | 877 276 7876, ext. |

Please understand that you are responsible for the accuracy of all project specifications, including any Armstrong guide specifications that you use.  ARMSTRONG SHALL NOT BE LIABLE FOR ANY DAMAGES ARISING OUT OF THE USE OF ANY OF ITS GUIDE SPECIFICATIONS.

# Consult your local Armstrong Architectural Specialty Representative or A/S Project Management Team prior to specifying any custom metal system.  Material, color, size and perforation options will affect feasibility of custom designs and should always be reviewed by Armstrong prior to releasing contract documents for bidding.

SECTION 09 54 24 (09545)

METAL PLANK CEILINGS

PART 1 - GENERAL

1.1  	RELATED DOCUMENTS

Drawings and general conditions of Contract, including General and Supplementary Conditions and Divisions-1 Specification sections apply to work of this section.

1.2	SUMMARY

A.	Section Includes:

1.	Metal ceiling panels.

2.	Suspension system.

- Wire hangers, clips, wall angle moldings and accessories.

B.   Related Sections:

1.   Section 09 51 00 (09510) – Acoustical Ceilings

2.   Section 09 20 00 (09250) – Plaster and Gypsum Board

3.   Division 23 (15) Heating, Ventilating, and Air Conditioning

5.   Division 26 (16) Electrical Work

C. 	Alternates

1.	Prior Approval: Unless otherwise provided for in the Contract documents, proposed product substitutions may be submitted no later than twenty-five (25) working days prior to the date established for receipt of bids.  Acceptability of a proposed substitution is contingent upon the Architect’s review of the proposal for acceptability and approved products will be set forth by the Addenda.  If included in a Bid are substitute products which have not been approved by Addenda, the specified products shall be provided without additional compensation.

a.  Roll formed steel is not an acceptable substitute.

2.	Submittals which do not provide adequate data for the product evaluation will not be considered.  The proposed substitution must meet all requirements of this section, including but not neccessarily limited to, the following: Single source materials suppliers (if specified in Section 1.5); panel design, size, composition, color, and finish; suspension system component profiles and sizes; compliance with the referenced standards.

1.3	REFERENCES

A.	American Society for Testing and Materials (ASTM):

- ASTM A 366 “Standard Specification for Steel, Carbon Cold-Rolled Sheet, Commercial Quality”

- ASTM A 641 “Standard Specification for Zinc-Coated (Galvanized) Carbon Steel Wire”

- ASTM C 423 “Sound Absorption and Sound Absorption Coefficients by the Reverberation Room Method”

- ASTM E 84 “Standard Test Method for Surface Burning Characteristics of Building Materials”

- ASTM E 1414 Standard Test Method for Airborne Sound Attenuation Between Rooms Sharing a Common Ceiling Plenum.

- ASTM E 1264 Classification for Acoustical Ceiling Products

- ASTM E1477 “Standard Test for Luminous Reflectance Factor of Acoustical Materials by use of Integrating-Sphere Reflectometers”

B.   International Code Council Evaluation Service

AC156 - Acceptance Criteria for Seismic Qualification Testing of Non-structural Components

1.4	SUBMITTALS

- Product Data:  Submit manufacturer’s technical data for each type of ceiling unit and suspension system required.

- Samples:  Mimimum 12 inch x 12 inch samples of specified metal panel; 8 inch long samples of suspension system if applicable.

- Installation Instructions:  Submit manufacturer’s installation instructions as referenced in Part 3, Installation.

- Shop Drawings:  Submit manufacturer’s shop drawings as referenced in Part 3, Installation.

- Certifications:  Manufacturer’s certifications that products comply with specified requirements, including laboratory reports showing compliance with specified tests and standards.

1.5	QUALITY ASSURANCE

- Single-Source Responsibility:  Provide metal ceiling and suspension components produced by a single manufacturer with resources adequate to deliver a product of consistent quality in terms of appearance and physical properties for all project scopes without risk of delay or interruption.

- Fire Performance Characteristics:  Identify ceiling components with appropriate applicable, testing, including:

1.	Surface Burning Characteristics:  As follows, tested per ASTM E 84 and complying with Class A  fire performance as follows:

a.	Flame Spread:  25 or less

- Seismic Performance:  System seismic performance verified through full-scale testing in accordance with ICC-ES – AC-156 Acceptance Criteria for Seismic Qualification Testing of Non-Structural components.

- Coordination of Work:  Coordinate ceiling work with installers of related work including, but not limited to building insulation, gypsum board, light fixtures, mechanical systems, electrical systems, and sprinklers.

# 1.6   DELIVERY, STORAGE, AND HANDLING

      - Deliver system components in manufacturer’s original, unopened packages clearly labeled with the following information: item number and quantity, manufacturer’s name and address, client name and address and site address.

      - Store components in a fully enclosed dry space where they will be protected against damage from moisture, direct sunlight, surface contamination and other construction activities.

      - Exercise care in handling components to prevent damage to the surfaces and edges and prevent distortion or other physical damage.

# 1.7     PROJECT CONDITIONS

- Space Enclosure:

  - Building areas to receive ceilings shall be free of construction dust and debris. Products may be installed where temperatures are between 32oF (0°C) and 120°F (49°C) and in spaces before the building is enclosed, where HVAC systems are cycled or not operating.  Such installations shall not be exposed to abnormal conditions, namely: chemical fumes, presence of standing water, or contact with moisture, as could result from condensations or building leaks.  These products cannot be used in exterior applications unless the system has been specifically designed and approved for exterior application.

- 1.8	WARRANTY

- Ceiling System: Submit a written warranty executed by the manufacturer, agreeing to repair or replace panels that fail within the warranty period. Failures include, but are not limited to:

  - Ceiling Panels and Suspension System: Rust and manufacturing defects.

- Warranty Period:

  - One (1) year from date of substantial completion.

- The Warranty shall not deprive the Owner of other rights the Owner may have under other provisions of the Contract Documents and will be in addition to and run concurrent with other warranties made by the Contractor under the requirements of the Contract Documents.

- Purpose and Limitations:

This information/data is provided by the manufacturer to better describe the product(s) and/or subject installation, solely for further evaluation by the Specifier.  The Manufacturer makes no representations, nor provides any warranty for the data provided except to the extent where it is applicable that it was prepared by an independent licensed professional engineer.  This information is not provided in lieu of the separate and independent evaluation and determination of suitability of these materials for the subject installation that is the responsibility of the specifier of their agents.

- 1.9	MAINTENANCE

- A.	Extra Materials:  Deliver extra materials to Owner.  Furnish extra materials described below that match products installed.  Packaged with protective covering for storage and identified with appropriate labels.

- 1.	Ceiling Units:  Furnish quanity of full-size units equal to 2 percent of amount installed.

  - Suspension System Components:  Furnish quantity of each exposed suspension component equal to 1 percent of amount installed.

- B.   Deliver extra stock to Owner’s representative.

- PART 2 - PRODUCTS

- 2.1	MANUFACTURER

- A.	Suspension Systems:

- 1.	Armstrong World Industries, Inc.

- B.	Ceiling Panels:

- 1.	Armstrong World Industries, Inc

    - SUSPENSION SYSTEM

- Suspension System:	AMP-1

- Product: Armstrong MetalWorks Fastrack Grid System.

- Components:

            - U-Profile Carrying Channel.

            - U-Profile Splice used to form continuous U-Profile carrying channel.

            - Plug-in clip provided for attachment to U-Profile carrying channel.

            - “C” Profile Trim Strips shall be commercial-quality galvanized steel.

            - Hanger for C Profile.

            - Wall anchor for C Profile.

            - Connector for C Profile.

            - BPM311.081 Pressure Spring to be provided as needed for hold down of cut panels at perimeter.

            - Wall Anchor

            - Wall Molding/Perimeter Treatment:  (To be determined based on panel size and design.)

- Finish:  All steel parts shall be chemically cleansed electro galvanized steel.

- Wall Molding Color: To match the actual color of the ceiling panel unless otherwise specified.

- “C” Profile Trim Strip: To Match the actual color of the ceiling unless otherwise specified.

- Hanger Wire: Hanger wire shall be galvanized carbon steel per ASTM A 641, soft temper, pre-stretched, with a yield stress load of at least three (3) times design load, but not less than 12 gauge (0.106”) diameter.

### 2.2.1 METAL CEILING PANELS

### A.  Ceiling Panels Type AMP-1:

- Product Type: Armstrong MetalWorks Fastrack System (Perforated) (Non-Perforated)

- Composition: 25 gauge minimum, electrogalvanized steel

- Perforations:

    - Pattern #:

    - Hole size:

    - On center spacing:

    - % Open area:

- Finish:  Scrubbable, powder coat, post painted (applied after forming)

- Color: As chosen by manufacturer’s available RAL colors.

- Size: As indicated on architectural drawings

- Edge Profile: Long edges return to form butt joints; short edges form hook.

- Noise Reduction Coefficient (NRC): ASTM C 423; (0.65) (0.90) (NA).

- Ceiling Attenuation Class (CAC): ASTM C 1414; (35) (NA)

- Flame Spread: ASTM E 1264; Class A per IBC

- Light Reflectance (LR): ASTM E 1477; White Panel: 0.61.

- Dimensional Stability:  L/360 ≤ 0.250 inch

- Acceptable Product: MetalWorks Fastrack System, as manufactured by Armstrong World Industries

- Accessories:

  - Fiberglass infill panel available – used to achieve up to 0.90 NRC performance.

  - Cutouts and apertures available – They are intended for use with audio speakers, air diffusers, flexible head sprinklers and certain light fixtures.  They are not intended for use with smoke detectors.

- PART 3 - EXECUTION

- 3.1	EXAMINATION

- Installer must inspect the area where the ceiling system is to be installed for conditions that may affect the work and notify the Contractor in writing of any unsatisfactory conditions before proceeding.

- All work above the ceiling system is to be satisfactorily completed prior to start of the ceiling installation.

- All unsatisfactory conditions potentially affecting the ceiling system are to be corrected prior to the start of ceiling installation.

- Do not proceed with installation until all wet work such as concrete, terrazzo, plastering and painting has been completed and thoroughly dried out.

- 3.2	PREPARATION

- A.   Examine construction and conditions under which system will be installed.  Do not proceed with installation until unsatisfactory conditions have been corrected.

  - INSTALLATION

      - Install the suspended ceiling system in accordance with the manufacturer’s shop drawings, installation instructions, applicable industry standards, and the governing code of jurisdiction.

      - Fastrack Installation Instructions:  LA295803

      - Installed panels should be free from damaged edges or other defects detrimental to appearance and function.

      - Install partial panels as shown on manufacturer’s shop drawings, but not less than one-half full size.

  - FIELD QUALITY CONTROL

A.   Deflection of any grid components shall not exceed 1/360 of the span.

3.5	ADJUSTING AND CLEANING

Adjust ceiling components to provide a consistent finish and appearance in conformity with pre-established tolerances and requirements.  All panels showing signs of damage, either in finish or in form are to be replaced.  All exposed surfaces are to be cleaned of any dirt, grease, fingerprints and marks or other imperfections with cleaning materials recommended by the manufacturer.

END OF SECTION