Copyright 2018 AIA
MasterSpec Full Length
03/18

PRODUCT MASTERSPEC LICENSED BY AVITRU, LLC TO CERTAINTEED CORPORATION.

Copyright 2017 by The American Institute of Architects (AIA)

Exclusively published and distributed by AVITRU, LLC for the AIA
This Product MasterSpec Section is licensed by AVITRU, LLC to CertainTeed Corporation ("Licensee").
This Product MasterSpec Section modifies the original MasterSpec text and does not include the full content of the original MasterSpec Section.
Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, Avitru or The American Institute of Architects (AIA). Neither AIA nor Avitru are liable in any way for such revisions or for the use of this Product MasterSpec Section by any end user. A qualified design professional should review and edit the document to suit project requirements.

For more information, contact CertainTeed Corporation, 20 Moores Road, Malvern, PA 19355; Phone: (800) 233-8990; Website: www.certainteed.com; Email: salessupportgroup@certainteed.com.

For information about MasterSpec, contact Avitru at (800) 424-5080 or visit avitru.com.
SECTION 230713 - DUCT INSULATION
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single-File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Access Product MasterSpec Sections:

<Double click here to view the list of manufacturer Sections available at ProductMasterSpec.com.>
Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section includes insulating the following duct services:

The list below matches the various systems in the schedule articles. Coordinate the revision of list with "Duct Insulation Schedule, General," "Indoor Duct and Plenum Insulation Schedule," and "Aboveground, Outdoor Duct and Plenum Insulation Schedule" articles.

1. Indoor, concealed supply and outdoor air.

2. Indoor, exposed supply and outdoor air.

3. Indoor, concealed return located in unconditioned space.

4. Indoor, exposed return located in unconditioned space.

5. Indoor, concealed, Type I, commercial, kitchen hood exhaust.

6. Indoor, exposed, Type I, commercial, kitchen hood exhaust.

7. Indoor, concealed oven and warewash exhaust.

8. Indoor, exposed oven and warewash exhaust.

9. Indoor, concealed exhaust between isolation damper and penetration of building exterior.

10. Indoor, exposed exhaust between isolation damper and penetration of building exterior.

11. Outdoor, concealed supply and return.

12. Outdoor, exposed supply and return.

B. Related Sections:

Retain Sections in subparagraphs below that contain requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Section 230716 "HVAC Equipment Insulation."

2. Section 230719 "HVAC Piping Insulation."

3. Section 233113 "Metal Ducts" for duct liners.

1.3 ACTION SUBMITTALS

A. Product Data: For each type of product indicated. Include thermal conductivity, water-vapor permeance thickness, and jackets (both factory- and field-applied if any).

B. Sustainable Design Submittals:

"Product Data" Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes. Coordinate with requirements for adhesives.

1. Product Data: For adhesives, indicating VOC content.

"Laboratory Test Reports" Subparagraph below applies to LEED 2009 for Schools, LEED v4, IgCC, ASHRAE 189.1, and Green Globes. Coordinate with requirements for adhesives.

2. Laboratory Test Reports: For adhesives, indicating compliance with requirements for low-emitting materials.
"Product Data" Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes. Coordinate with requirements for paints and coatings.

3. Product Data: For coatings, indicating VOC content.

"Laboratory Test Reports" Subparagraph below applies to LEED 2009 for Schools, LEED v4, IgCC, ASHRAE 189.1, and Green Globes. Coordinate with requirements for paints and coatings.

4. Laboratory Test Reports: For coatings, indicating compliance with requirements for low-emitting materials.
"Product Data" Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes. Coordinate with requirements for sealants.

5. Product Data: For sealants, indicating VOC content.

"Laboratory Test Reports" Subparagraph below applies to LEED 2009 for Schools, LEED v4, IgCC, ASHRAE 189.1, and Green Globes. Coordinate with requirements for sealants.

6. Laboratory Test Reports: For sealants, indicating compliance with requirements for low-emitting materials.
C. Shop Drawings: Include plans, elevations, sections, details, and attachments to other work.

1. Detail application of protective shields, saddles, and inserts at hangers for each type of insulation and hanger.

2. Detail insulation application at elbows, fittings, dampers, specialties and flanges for each type of insulation.

3. Detail application of field-applied jackets.

4. Detail application at linkages of control devices.

Retain first paragraph below to verify products with Samples.

D. Samples: For each type of insulation and jacket indicated. Identify each Sample, describing product and intended use. Sample sizes are as follows:

1. Sheet Form Insulation Materials: 12 inches (300 mm) square.

2. Sheet Jacket Materials: 12 inches (300 mm) square.

3. Manufacturer's Color Charts: For products where color is specified, show the full range of colors available for each type of finish material.

1.4 INFORMATIONAL SUBMITTALS

Coordinate first paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as supplemented in "Quality Assurance" Article.

A. Qualification Data: For qualified Installer.

Retain first paragraph below if surface-burning characteristics specified in "Quality Assurance" Article are specified to be verified by an independent testing agency.

B. Material Test Reports: From a qualified testing agency acceptable to authorities having jurisdiction indicating, interpreting, and certifying test results for compliance of insulation materials, sealers, attachments, cements, and jackets, with requirements indicated. Include dates of tests and test methods employed.

Retain paragraph below if Contractor is responsible for field quality-control testing and inspecting.

C. Field quality-control reports.

1.5 QUALITY ASSURANCE

Retain first paragraph below if available at Project location. Apprenticeship programs are usually associated with union shops. Other craft training programs are available.

A. Installer Qualifications: Skilled mechanics who have successfully completed an apprenticeship program or another craft training program certified by the Department of Labor, Bureau of Apprenticeship and Training.

When fire-performance characteristics are important requirements, verify surface-burning characteristics of insulation materials by an independent testing agency and require test report submittals.

B. Surface-Burning Characteristics: For insulation and related materials, as determined by testing identical products in accordance with ASTM E84, by a testing agency acceptable to authorities having jurisdiction. Factory label insulation and jacket materials and adhesive, mastic, tapes, and cement material containers, with appropriate markings of applicable testing agency.

1. Insulation Installed Indoors: Flame-spread index of 25 or less, and smoke-developed index of 50 or less.

2. Insulation Installed Outdoors: Flame-spread index of 75 or less, and smoke-developed index of 150 or less.

If retaining "Mockups" Paragraph below, indicate location, size, and other details of mockups on Drawings or by inserts. Revise if only one mockup is required.

C. Mockups: Before installing insulation, build mockups for each type of insulation and finish listed below to demonstrate quality of insulation application and finishes. Build mockups in the location indicated or, if not indicated, as directed by Architect. Use materials indicated for the completed Work.

1. Ductwork Mockups:

a. One 10-foot (3-m) section each of rectangular and round straight duct.

b. One each of a 90-degree mitered round and rectangular elbow, and one each of a 90-degree radius round and rectangular elbow.

c. One rectangular branch takeoff and one round branch takeoff from a rectangular duct. One round tee fitting.

d. One rectangular and round transition fitting.

e. Four support hangers for round and rectangular ductwork.

f. Each type of damper and specialty.

2. For each mockup, fabricate cutaway sections to allow observation of application details for insulation materials, adhesives, mastics, attachments, and jackets.

3. Notify Architect seven days in advance of dates and times when mockups will be constructed.

4. Obtain Architect's approval of mockups before starting insulation application.

Retain first subparagraph below if mockups are not only for establishing appearance factors.

5. Approval of mockups does not constitute approval of deviations from the Contract Documents contained in mockups unless Architect specifically approves such deviations in writing.

6. Maintain mockups during construction in an undisturbed condition as a standard for judging the completed Work.

7. Demolish and remove mockups when directed.

1.6 DELIVERY, STORAGE, AND HANDLING

Retain this article to require shipping container markings. Container marking is an option in ASTM standards; default condition does not include the marking in this article unless specified in the Contract.

A. Packaging: Insulation material containers shall be marked by manufacturer with appropriate ASTM standard designation, type and grade, and maximum use temperature.

1.7 COORDINATION

A. Coordinate sizes and locations of supports, hangers, and insulation shields specified in Section 230529 "Hangers and Supports for HVAC Piping and Equipment."

B. Coordinate clearance requirements with duct Installer for duct insulation application. Before preparing ductwork Shop Drawings, establish and maintain clearance requirements for installation of insulation and field-applied jackets and finishes and for space required for maintenance.

C. Coordinate installation and testing of heat tracing.

1.8 SCHEDULING

A. Schedule insulation application after pressure testing systems and, where required, after installing and testing heat tracing. Insulation application may begin on segments that have satisfactory test results.

B. Complete installation and concealment of plastic materials as rapidly as possible in each area of construction.

PART 2 -  PRODUCTS

2.1 INSULATION MATERIALS

If retaining more than one type of insulation in this article, indicate where each type applies in insulation system schedules.

A. Comply with requirements in "Duct Insulation Schedule, General," "Indoor Duct and Plenum Insulation Schedule," and "Aboveground, Outdoor Duct and Plenum Insulation Schedule" articles for where insulating materials shall be applied.

See "Product Characteristics" Article in the Evaluations for comparisons and temperature ranges for insulation material properties.

B. Products shall not contain asbestos, lead, mercury, or mercury compounds.

C. Products that come in contact with stainless steel shall have a leachable chloride content of less than 50 ppm when tested in accordance with ASTM C871.

D. Insulation materials for use on austenitic stainless steel shall be qualified as acceptable in accordance with ASTM C795.

E. Foam insulation materials shall not use CFC or HCFC blowing agents in the manufacturing process.

"Flexible Elastomeric Insulation" Paragraph below is unsuitable for temperatures lower than minus 70 deg F (minus 57 deg C) and higher than 220 deg F (104 deg C).

F. Flexible Elastomeric Insulation: Closed-cell, sponge- or expanded-rubber materials. Comply with ASTM C534, Type II for sheet materials.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. Aeroflex USA, Inc.

b. Armacell LLC.

c. K-Flex USA.
d. <Insert manufacturer's name>.
For operating temperatures higher than 250 deg F (121 deg C), use blanket insulation in first paragraph below. Retain ASTM C1290 types as follows: Type I for insulation without jackets, Type II for insulation with vinyl jackets, and Type III for insulation with FSK or FSP jackets.

G. Mineral-Fiber Blanket Insulation: Mineral or glass fibers bonded with a thermosetting resin. Comply with ASTM C553, Type II and ASTM C1290, [Type I] [Type II with factory-applied vinyl jacket] [Type III with factory-applied FSK jacket] [Type III with factory-applied FSP jacket]. Factory-applied jacket requirements are specified in "Factory-Applied Jackets" Article.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or comparable product from manufacturers listed.

1. Basis-of-Design Product: Subject to compliance with requirements, provide CertainTeed Corporation; [Sustainable Insulation] [SoftTouch™ Duct Wrap] [WideWrap™ Duct Wrap] [Marine Thermal Blanket Insulation] or comparable product by one of the following:
a. Johns Manville; a Berkshire Hathaway company.

b. Knauf Insulation.

c. Manson Insulation Inc.

d. Owens Corning.
e. <Insert manufacturer's name>.
For operating temperatures higher than 250 deg F (121 deg C), use board insulation in first paragraph below. The most common jacket for ductwork and plenum applications is FSK.

H. Mineral-Fiber Board Insulation: Mineral or glass fibers bonded with a thermosetting resin. Comply with ASTM C612, Type IA or Type IB. For duct and plenum applications, provide insulation [without factory-applied jacket] [with factory-applied ASJ] [with factory-applied FSK jacket]. Factory-applied jacket requirements are specified in "Factory-Applied Jackets" Article.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or comparable product from manufacturers listed.

1. Basis-of-Design Product: Subject to compliance with requirements, provide CertainTeed Corporation; CertaPRO® Commercial Board or comparable product by one of the following:
a. Johns Manville; a Berkshire Hathaway company.

b. Knauf Insulation.

c. Manson Insulation Inc.

d. Owens Corning.
e. <Insert manufacturer's name>.
Pipe and tank insulation is used for large-diameter piping and vessels. ASJ is commonly used.

I. Mineral-Fiber, Pipe and Tank Insulation: Mineral or glass fibers bonded with a thermosetting resin. Semirigid board material with factory-applied [ASJ] [FSK jacket] complying with ASTM C1393, Type II or Type IIIA Category 2, or with properties similar to ASTM C612, Type IB. Nominal density is 2.5 lb/cu. ft. (40 kg/cu. m) or more. Thermal conductivity (k-value) at 100 deg F (55 deg C) is 0.29 Btu x in./h x sq. ft. x deg F (0.042 W/m x K) or less. Factory-applied jacket requirements are specified in "Factory-Applied Jackets" Article.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or comparable product from manufacturers listed.

1. Basis-of-Design Product: Subject to compliance with requirements, provide CertainTeed Corporation; CrimpWrap™ Crimped Pipe and Tank Wrap or comparable product by one of the following:
a. Johns Manville; a Berkshire Hathaway company.

b. Knauf Insulation.

c. Manson Insulation Inc.

d. Owens Corning.
e. <Insert manufacturer's name>.
J. Polyolefin: Unicellular, polyethylene thermal plastic insulation. Comply with ASTM C534 or ASTM C1427, Type I, Grade 1 for tubular materials and Type II, Grade 1 for sheet materials.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by the following:

a. Armacell LLC.
b. <Insert manufacturer's name>.
2.2 FIRE-RATED INSULATION SYSTEMS

Retain this article for fire-rated insulation, which is sometimes used in lieu of fire-rated assemblies. A common application is for Type I, commercial, kitchen hood exhaust ductwork. See the Evaluations.

A. Fire-Rated Board: Structural-grade, press-molded, xonolite calcium silicate, fireproofing board suitable for operating temperatures up to 1700 deg F (927 deg C). Comply with ASTM C656, Type II, Grade 6. Tested and certified to provide a [1] [2]-hour fire rating by an NRTL acceptable to authorities having jurisdiction.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by the following:

a. Johns Manville; a Berkshire Hathaway company.
b. <Insert manufacturer's name>.
B. Fire-Rated Blanket: High-temperature, flexible, blanket insulation with FSK jacket that is tested and certified to provide a [1] [2]-hour fire rating by an NRTL acceptable to authorities having jurisdiction.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. 3M.

b. Johns Manville; a Berkshire Hathaway company.

c. Nelson Firestop; a brand of Emerson Industrial Automation.

d. Thermal Ceramics.

e. Unifrax Corporation.
f. <Insert manufacturer's name>.
2.3 ADHESIVES

Military Specification in this article was the only standard available when this Section was written. MIL-A-3316C was last updated in October 1987.

A. Materials shall be compatible with insulation materials, jackets, and substrates and for bonding insulation to itself and to surfaces to be insulated unless otherwise indicated.

Product attributes in first paragraph below are based on Foster Brand products; there are variations among manufacturers.

B. Flexible Elastomeric and Polyolefin Adhesive: Comply with MIL-A-24179A, Type II, Class I.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. Aeroflex USA, Inc.

b. Armacell LLC.

c. Foster Brand; H. B. Fuller Construction Products.

d. K-Flex USA.
e. <Insert manufacturer's name>.
Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes. VOC content limit is that for plastic foam adhesives.

2. Adhesives shall have a VOC content of [50] <Insert value> g/L or less.

Subparagraph below applies to LEED 2009 for Schools Credit IEQ 4.1.

3. Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Subparagraph below applies to LEED v4.

4. Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Subparagraph below applies to IgCC.

5. Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers." Formaldehyde emissions shall not exceed 9 mcg/cu. m or 7 ppb, whichever is less.

Subparagraph below applies to ASHRAE 189.1.

6. Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Subparagraph below applies to Green Globes.

7. Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers." The building concentration of formaldehyde shall not exceed half of the indoor recommended exposure limit, or 33 mcg/cu. m, and that of acetaldehyde shall not exceed 9 mcg/cu. m.
C. Mineral-Fiber Adhesive: Comply with MIL-A-3316C, Class 2, Grade A.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. Childers Brand; H. B. Fuller Construction Products.

b. Eagle Bridges - Marathon Industries.

c. Foster Brand; H. B. Fuller Construction Products.

d. Mon-Eco Industries, Inc.
e. <Insert manufacturer's name>.
Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes. VOC content limit is that for fiberglass.

2. Fiberglass adhesive shall have a VOC content of 80 g/L or less when calculated in accordance with 40 CFR 59, Subpart D (EPA Method 24).
Subparagraph below applies to LEED 2009 for Schools Credit IEQ 4.1.

3. Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Subparagraph below applies to LEED v4.

4. Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Subparagraph below applies to IgCC.

5. Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers." Formaldehyde emissions shall not exceed 9 mcg/cu. m or 7 ppb, whichever is less.

Subparagraph below applies to ASHRAE 189.1.

6. Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Subparagraph below applies to Green Globes.

7. Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers." The building concentration of formaldehyde shall not exceed half of the indoor recommended exposure limit, or 33 mcg/cu. m, and that of acetaldehyde shall not exceed 9 mcg/cu. m.
D. ASJ Adhesive, and FSK Jacket Adhesive: Comply with MIL-A-3316C, Class 2, Grade A for bonding insulation jacket lap seams and joints.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. Childers Brand; H. B. Fuller Construction Products.

b. Eagle Bridges - Marathon Industries.

c. Foster Brand; H. B. Fuller Construction Products.

d. Mon-Eco Industries, Inc.
e. <Insert manufacturer's name>.
Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes. VOC content limit is that for contact adhesive.

2. Adhesive shall have a VOC content of 80 g/L or less when calculated in accordance with 40 CFR 59, Subpart D (EPA Method 24).
Subparagraph below applies to LEED 2009 for Schools Credit IEQ 4.1.

3. Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Subparagraph below applies to LEED v4.

4. Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Subparagraph below applies to IgCC.

5. Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers." Formaldehyde emissions shall not exceed 9 mcg/cu. m or 7 ppb, whichever is less.

Subparagraph below applies to ASHRAE 189.1.

6. Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Subparagraph below applies to Green Globes.

7. Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers." The building concentration of formaldehyde shall not exceed half of the indoor recommended exposure limit, or 33 mcg/cu. m, and that of acetaldehyde shall not exceed 9 mcg/cu. m.
E. PVC Jacket Adhesive: Compatible with PVC jacket.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. Dow Corning Corporation.

b. Johns Manville; a Berkshire Hathaway company.

c. P.I.C. Plastics, Inc.

d. Speedline Corporation.
e. <Insert manufacturer's name>.
Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes. VOC content limit is that for contact adhesive.

2. Adhesive shall have a VOC content of 80 g/L or less when calculated in accordance with 40 CFR 59, Subpart D (EPA Method 24).
Subparagraph below applies to LEED 2009 for Schools Credit IEQ 4.1.

3. Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Subparagraph below applies to LEED v4.

4. Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Subparagraph below applies to IgCC.

5. Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers." Formaldehyde emissions shall not exceed 9 mcg/cu. m or 7 ppb, whichever is less.

Subparagraph below applies to ASHRAE 189.1.

6. Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Subparagraph below applies to Green Globes.

7. Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers." The building concentration of formaldehyde shall not exceed half of the indoor recommended exposure limit, or 33 mcg/cu. m, and that of acetaldehyde shall not exceed 9 mcg/cu. m.
2.4 MASTICS AND COATINGS

Mastic and coating terminology is used interchangeably in this article. Manufacturers refer to vapor barrier formulations and vapor-retarder formulations as "mastics" or "coatings." Low-permeance mastics and coatings are termed "vapor retarders." Products with a perm rating of greater than 1.0 are called "breathable." Consider ambient conditions and operating temperatures when selecting mastics and coatings. Consider using water-based mastics and coatings for environmental reasons.

LEED 2009 IEQ Credit 4.1 does not address requirements for mastics and coatings. LEED 2009 IEQ Credit 4.2 does address requirements for mastics and coatings. LEED v4 EQ Credit "Low-Emitting Materials" does address requirements for mastics and coatings.

A. Materials shall be compatible with insulation materials, jackets, and substrates.

"VOC Content" Subparagraph below applies to LEED 2009 NC, CI, and CS Credit IEQ 4.2.

1. VOC Content: [300] <Insert value> g/L or less.

"Low-Emitting Materials" Subparagraph below applies to LEED 2009 for Schools.

2. Low-Emitting Materials: Mastic coatings shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

"VOC Content" and "Low-Emitting Materials" Subparagraphs below apply to LEED v4.

3. VOC Content: [300] <Insert value> g/L or less.

4. Low-Emitting Materials: Mastic coatings shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

"VOC Content" and "Low-Emitting Materials" Subparagraphs below apply to IgCC.

5. VOC Content: [300] <Insert value> g/L or less.

6. Low-Emitting Materials: Mastic coatings shall comply with the requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers." Formaldehyde emissions shall not exceed 9 mcg/cu. m or 7 ppb, whichever is less.

VOC Content" and "Low-Emitting Materials" Subparagraphs below apply to ASHRAE 189.1.

7. VOC Content: [300] <Insert value> g/L or less.

8. Low-Emitting Materials: Mastic coatings shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

"VOC Emissions" Subparagraph below applies to Green Globes.

9. VOC Emissions: Mastic coatings shall contain no more than half of the chronic REL of VOCs when tested in accordance with the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers." The building concentration of formaldehyde shall not exceed half of the indoor recommended exposure limit or 33 mcg/cu. m and that of acetaldehyde shall not exceed 9 mcg/cu. m.
Verify that products listed comply with water-vapor permeance. Require proof of performance and certified test reports from vapor-barrier mastic manufacturer to support product literature claims.

Retain one of four paragraphs below. Consider insulation type and operating conditions when selecting mastics and coatings.

B. Vapor-Retarder Mastic: Water based; suitable for indoor use on below ambient services.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. Childers Brand; H. B. Fuller Construction Products.

b. Foster Brand; H. B. Fuller Construction Products.

c. Knauf Insulation.

d. Vimasco Corporation.
e. <Insert manufacturer's name>.
2. Water-Vapor Permeance: Comply with ASTM C755, Section 7.2.2, Table 2, for insulation type and service conditions.

3. Service Temperature Range: Minus 20 to plus 180 deg F (Minus 29 to plus 82 deg C).

Retain MIL-PRF-19565C in first subparagraph below for vapor-retarder mastics and coatings if applicable to project.

4. Comply with MIL-PRF-19565C, Type II, for permeance requirements[, with supplier listing on DOD QPD - Qualified Products Database].

5. Color: [White] <Insert color>.

Retain solvent-based "Vapor-Retarder Mastic" Paragraph below if low-VOC mastics and coatings are not required, or if a lower permeance is required.

C. Vapor-Retarder Mastic: Solvent based; suitable for indoor use on below ambient services.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. Childers Brand; H. B. Fuller Construction Products.

b. Eagle Bridges - Marathon Industries.

c. Foster Brand; H. B. Fuller Construction Products.

d. Mon-Eco Industries, Inc.
e. <Insert manufacturer's name>.
2. Water-Vapor Permeance: Comply with ASTM C755, Section 7.2.2, Table 2, for insulation type and service conditions.

3. Service Temperature Range: 0 to 180 deg F (Minus 18 to plus 82 deg C).

4. Color: [White] <Insert color>.

D. Vapor-Retarder Mastic: Solvent based; suitable for outdoor use on below ambient services.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. Childers Brand; H. B. Fuller Construction Products.

b. Eagle Bridges - Marathon Industries.

c. Foster Brand; H. B. Fuller Construction Products.
d. <Insert manufacturer's name>.
2. Water-Vapor Permeance: Comply with ASTM C755, Section 7.2.2, Table 2, for insulation type and service conditions.

3. Service Temperature Range: Minus 50 to plus 220 deg F (Minus 46 to plus 104 deg C).

4. Color: [White] <Insert color>.

E. Breather Mastic: Water based; suitable for indoor and outdoor use on above ambient services.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. Childers Brand; H. B. Fuller Construction Products.

b. Eagle Bridges - Marathon Industries.

c. Foster Brand; H. B. Fuller Construction Products.

d. Knauf Insulation.

e. Mon-Eco Industries, Inc.

f. Vimasco Corporation.
g. <Insert manufacturer's name>.
2. Water-Vapor Permeance: ASTM E96, greater than 1.0 perm (0.66 metric perms) at manufacturer's recommended dry film thickness.

3. Service Temperature Range: Minus 20 to plus 180 deg F (Minus 29 to plus 82 deg C).

4. Color: [White] <Insert color>.

2.5 LAGGING ADHESIVES

A. Description: Comply with MIL-A-3316C, Class I, Grade A and shall be compatible with insulation materials, jackets, and substrates.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. Childers Brand; H. B. Fuller Construction Products.

b. Foster Brand; H. B. Fuller Construction Products.

c. Vimasco Corporation.
d. <Insert manufacturer's name>.
Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes. VOC content limit is that for adhesives for porous materials other than wood.

2. Adhesives shall have a VOC content of [50] <Insert value> g/L or less.
Subparagraph below applies to LEED 2009 for Schools Credit IEQ 4.1.

3. Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Subparagraph below applies to LEED v4.

4. Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Subparagraph below applies to IgCC.

5. Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers." Formaldehyde emissions shall not exceed 9 mcg/cu. m or 7 ppb, whichever is less.

Subparagraph below applies to ASHRAE 189.1.

6. Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Subparagraph below applies to Green Globes.

7. Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers." The building concentration of formaldehyde shall not exceed half of the indoor recommended exposure limit, or 33 mcg/cu. m, and that of acetaldehyde shall not exceed 9 mcg/cu. m.
8. Fire-resistant, water-based lagging adhesive and coating for use indoors to adhere fire-resistant lagging cloths over duct insulation.

9. Service Temperature Range: 0 to plus 180 deg F (Minus 18 to plus 82 deg C).

10. Color: White.

2.6 SEALANTS

Materials in first paragraph below are for sealing metal jacket seams and joints.

A. FSK and Metal Jacket Flashing Sealants:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. Childers Brand; H. B. Fuller Construction Products.

b. Eagle Bridges - Marathon Industries.

c. Foster Brand; H. B. Fuller Construction Products.

d. Mon-Eco Industries, Inc.
e. <Insert manufacturer's name>.
2. Materials shall be compatible with insulation materials, jackets, and substrates.

3. Fire- and water-resistant, flexible, elastomeric sealant.

4. Service Temperature Range: Minus 40 to plus 250 deg F (Minus 40 to plus 121 deg C).

5. Color: Aluminum.

Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes.

6. Sealant shall have a VOC content of 420 g/L or less.
Subparagraph below applies to LEED 2009 for Schools Credit IEQ 4.1.

7. Sealant shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Subparagraph below applies to LEED v4.

8. Sealant shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Subparagraph below applies to IgCC.

9. Sealant shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers." Formaldehyde emissions shall not exceed 9 mcg/cu. m or 7 ppb, whichever is less.

Subparagraph below applies to ASHRAE 189.1.

10. Sealant shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Subparagraph below applies to Green Globes.

11. Sealant shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers." The building concentration of formaldehyde shall not exceed half of the indoor recommended exposure limit, or 33 mcg/cu. m, and that of acetaldehyde shall not exceed 9 mcg/cu. m.
B. ASJ Flashing Sealants, and Vinyl and PVC Jacket Flashing Sealants:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by the following:

a. Childers Brand; H. B. Fuller Construction Products.
b. <Insert manufacturer's name>.
2. Materials shall be compatible with insulation materials, jackets, and substrates.

3. Fire- and water-resistant, flexible, elastomeric sealant.

4. Service Temperature Range: Minus 40 to plus 250 deg F (Minus 40 to plus 121 deg C).

5. Color: White.

Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes.

6. Sealant shall have a VOC content of 420 g/L or less.
Subparagraph below applies to LEED 2009 for Schools Credit IEQ 4.1.

7. Sealant shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Subparagraph below applies to LEED v4.

8. Sealant shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Subparagraph below applies to IgCC.

9. Sealant shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers." Formaldehyde emissions shall not exceed 9 mcg/cu. m or 7 ppb, whichever is less.

Subparagraph below applies to ASHRAE 189.1.

10. Sealant shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Subparagraph below applies to Green Globes.

11. Sealant shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers." The building concentration of formaldehyde shall not exceed half of the indoor recommended exposure limit, or 33 mcg/cu. m, and that of acetaldehyde shall not exceed 9 mcg/cu. m.
2.7 FACTORY-APPLIED JACKETS

Coordinate types of factory-applied jacket insulation materials selected and types of factory-applied jackets indicated in insulation system schedules.

For insulation materials with factory-applied jackets for use on applications above 140 deg F (60 deg C), specify sufficient insulation thickness to maintain outer surface temperature of insulation below 140 deg F (60 deg C). 140 deg F (60 deg C) surface temperature is set by OSHA for personnel protection.

Knauf is the only mineral-fiber insulation manufacturer that offers factory-applied FSP jacket for blanket insulation. CertainTeed and Johns Manville offer a vinyl jacket, but it does not comply with ASTM C1136. Owens Corning does not offer an FSP or a vinyl product.

A. Insulation system schedules indicate factory-applied jackets on various applications. When factory-applied jackets are indicated, comply with the following:

1. ASJ: White, kraft-paper, fiberglass-reinforced scrim with aluminum-foil backing; complying with ASTM C1136, Type I.

2. ASJ-SSL: ASJ with self-sealing, pressure-sensitive, acrylic-based adhesive covered by a removable protective strip; complying with ASTM C1136, Type I.

3. FSK Jacket: Aluminum-foil, fiberglass-reinforced scrim with kraft-paper backing; complying with ASTM C1136, Type II.

4. FSP Jacket: Aluminum-foil, fiberglass-reinforced scrim with polyethylene backing; complying with ASTM C1136, Type II.

5. Vinyl Jacket: White vinyl with a permeance of 1.3 perms (0.86 metric perm) when tested in accordance with ASTM E96/E96M, Procedure A, and complying with NFPA 90A and NFPA 90B.

2.8 FIELD-APPLIED FABRIC-REINFORCING MESH

Both glass-fiber- and polyester-fabric-reinforcing meshes are acceptable.

Retain both paragraphs below to give Contractor option to use either glass-fiber or polyester fabric.

A. Woven Glass-Fiber Fabric: Approximately 6 oz./sq. yd. (203 g/sq. m) with a thread count of 5 strands by 5 strands/sq. in. (2 strands by 2 strands/sq. mm) for covering ducts.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by the following:

a. Childers Brand; H. B. Fuller Construction Products.
b. <Insert manufacturer's name>.
B. Woven Polyester Fabric: Approximately 1 oz./sq. yd. (34 g/sq. m) with a thread count of 10 strands by 10 strands/sq. in. (4 strands by 4 strands/sq. mm), in a Leno weave, for ducts.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. Foster Brand; H. B. Fuller Construction Products.

b. Vimasco Corporation.
c. <Insert manufacturer's name>.
2.9 FIELD-APPLIED CLOTHS

A. Woven Glass-Fiber Fabric: Comply with MIL-C-20079H, Type I, plain weave, and presized a minimum of 8 oz./sq. yd. (271 g/sq. m).

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by the following:

a. Alpha Associates, Inc.
b. <Insert manufacturer's name>.
2.10 FIELD-APPLIED JACKETS

Insulation jackets in this article are for field application. ASTM C921, Type I, is for use over insulation on ducts operating at below ambient temperatures at least part of the time or where a vapor barrier is required. ASTM C921, Type II, is for use over insulation on ducts operating above ambient temperatures or where a vapor retarder is not required.

A. Field-applied jackets shall comply with ASTM C921, Type I, unless otherwise indicated.

A properly sealed FSK jacket, common with most forms of factory-applied jackets for mineral-fiber insulation, complies with vapor-retarder requirements in ASTM C921, Type I.

B. FSK Jacket: Aluminum-foil-face, fiberglass-reinforced scrim with kraft-paper backing.

Although other thicknesses for PVC jackets are available, a flame-spread index of 25 and a smoke-developed index of 50 apply only to thicknesses of 30 mils (0.8 mm) and less.

C. PVC Jacket: High-impact-resistant, UV-resistant PVC complying with ASTM D1784, Class 16354-C; thickness as scheduled; roll stock ready for shop or field cutting and forming. Thickness is indicated in field-applied jacket schedules.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. Johns Manville; a Berkshire Hathaway company.

b. P.I.C. Plastics, Inc.

c. Proto Corporation.

d. Speedline Corporation.
e. <Insert manufacturer's name>.
2. Adhesive: As recommended by jacket material manufacturer.

PVC jackets are available in several colors. Colored jackets may be used to replace field painting. UV rays fade colors in exterior applications. Some colors (black, gray, and white) do not fade as quickly as other colors (red, orange, and green). Colored jackets have different emissivity and are not recommended for outdoor use.

3. Color: [White] [Color-code jackets based on system. Color as selected by Architect].

D. Metal Jacket:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. ITW Insulation Systems; Illinois Tool Works, Inc.

b. RPR Products, Inc.
c. <Insert manufacturer's name>.
2. Aluminum Jacket: Comply with ASTM B209 (ASTM B209M), Alloy 3003, 3005, 3105, or 5005, Temper H-14.

a. [Sheet and roll stock ready for shop or field sizing] [Factory cut and rolled to size].

b. Finish and thickness are indicated in field-applied jacket schedules.

Among the three moisture barriers in first subparagraph below, 1-mil (0.025-mm) barrier provides the least protection against galvanic corrosion, 3-mil (0.075-mm) barrier offers better protection, and polysurlyn barrier offers the best protection. For most indoor applications, 1-mil (0.025-mm) barrier is adequate. For outdoor applications, select either 3-mil (0.075-mm) or polysurlyn barrier.

c. Moisture Barrier for Indoor Applications: [1-mil- (0.025-mm-) thick, heat-bonded polyethylene and kraft paper] [3-mil- (0.075-mm-) thick, heat-bonded polyethylene and kraft paper] [2.5-mil- (0.063-mm-) thick polysurlyn].

d. Moisture Barrier for Outdoor Applications: [3-mil- (0.075-mm-) thick, heat-bonded polyethylene and kraft paper] [2.5-mil- (0.063-mm-) thick polysurlyn].

3. Stainless Steel Jacket: ASTM A167 or ASTM A240/A240M.

a. [Sheet and roll stock ready for shop or field sizing] [Factory cut and rolled to size].

b. Material, finish, and thickness are indicated in field-applied jacket schedules.

Among the three moisture barriers in first subparagraph below, 1-mil (0.025-mm) barrier provides the least protection against galvanic corrosion, 3-mil (0.075-mm) barrier offers better protection, and polysurlyn barrier offers the best protection. For most indoor applications, 1-mil (0.025-mm) barrier is adequate.

c. Moisture Barrier for Indoor Applications: [1-mil- (0.025-mm-) thick, heat-bonded polyethylene and kraft paper] [3-mil- (0.075-mm-) thick, heat-bonded polyethylene and kraft paper] [2.5-mil- (0.063-mm-) thick polysurlyn].

d. Moisture Barrier for Outdoor Applications: [3-mil- (0.075-mm-) thick, heat-bonded polyethylene and kraft paper] [2.5-mil- (0.063-mm-) thick polysurlyn].

E. Self-Adhesive Outdoor Jacket: 60-mil- (1.5-mm-) thick, laminated vapor barrier and waterproofing membrane for installation over insulation located aboveground outdoors; consisting of a rubberized bituminous resin on a crosslaminated polyethylene film covered with [white] [stucco-embossed] aluminum-foil facing.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by the following:

a. Polyguard Products, Inc.
b. <Insert manufacturer's name>.
2.11 TAPES

Product performance is based on products manufactured by Venture Tape; there are slight variations among manufacturers.

A. ASJ Tape: White vapor-retarder tape matching factory-applied jacket with acrylic adhesive, complying with ASTM C1136.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. Avery Dennison Corporation, Specialty Tapes Division.

b. Compac Corporation.

c. Ideal Tape Co., Inc., an American Biltrite Company.

d. Knauf Insulation.

e. Venture Tape.
f. <Insert manufacturer's name>.
2. Width: 3 inches (75 mm).

3. Thickness: 11.5 mils (0.29 mm).

4. Adhesion: 90 ounces force/inch (1.0 N/mm) in width.

5. Elongation: 2 percent.

6. Tensile Strength: 40 lbf/inch (7.2 N/mm) in width.

7. ASJ Tape Disks and Squares: Precut disks or squares of ASJ tape.

B. FSK Tape: Foil-face, vapor-retarder tape matching factory-applied jacket with acrylic adhesive; complying with ASTM C1136.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. Avery Dennison Corporation, Specialty Tapes Division.

b. Compac Corporation.

c. Ideal Tape Co., Inc., an American Biltrite Company.

d. Knauf Insulation.

e. Venture Tape.
f. <Insert manufacturer's name>.
2. Width: 3 inches (75 mm).

3. Thickness: 6.5 mils (0.16 mm).

4. Adhesion: 90 ounces force/inch (1.0 N/mm) in width.

5. Elongation: 2 percent.

6. Tensile Strength: 40 lbf/inch (7.2 N/mm) in width.

7. FSK Tape Disks and Squares: Precut disks or squares of FSK tape.

C. PVC Tape: White vapor-retarder tape matching field-applied PVC jacket with acrylic adhesive; suitable for indoor and outdoor applications.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. Compac Corporation.

b. Ideal Tape Co., Inc., an American Biltrite Company.

c. Venture Tape.
d. <Insert manufacturer's name>.
2. Width: 2 inches (50 mm).

3. Thickness: 6 mils (0.15 mm).

4. Adhesion: 64 ounces force/inch (0.7 N/mm) in width.

5. Elongation: 500 percent.

6. Tensile Strength: 18 lbf/inch (3.3 N/mm) in width.

D. Aluminum-Foil Tape: Vapor-retarder tape with acrylic adhesive.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. Avery Dennison Corporation, Specialty Tapes Division.

b. Compac Corporation.

c. Ideal Tape Co., Inc., an American Biltrite Company.

d. Knauf Insulation.

e. Venture Tape.
f. <Insert manufacturer's name>.
2. Width: 2 inches (50 mm).

3. Thickness: 3.7 mils (0.093 mm).

4. Adhesion: 100 ounces force/inch (1.1 N/mm) in width.

5. Elongation: 5 percent.

6. Tensile Strength: 34 lbf/inch (6.2 N/mm) in width.

2.12 SECUREMENTS

A. Bands:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. ITW Insulation Systems; Illinois Tool Works, Inc.

b. RPR Products, Inc.
c. <Insert manufacturer's name>.
Wing seals are primarily used for fastening bands together. Closed seals are occasionally used for large, 84-inch- (2130-mm-) diameter applications and where fastening bands are used with springs. Wing seals are reusable; closed seals are not.

2. Stainless Steel: ASTM A167 or ASTM A240/A240M, [Type 304] [or] [Type 316]; 0.015 inch (0.38 mm) thick, [1/2 inch (13 mm)] [3/4 inch (19 mm)] wide with [wing seal] [or] [closed seal].

3. Aluminum: ASTM B209 (ASTM B209M), Alloy 3003, 3005, 3105, or 5005; Temper H-14, 0.020 inch (0.51 mm) thick, [1/2 inch (13 mm)] [3/4 inch (19 mm)] wide with [wing seal] [or] [closed seal].

Springs are used for large, 84-inch- (2130-mm-) diameter applications and on applications with rapid changes in expansion and contraction.

4. Springs: Twin spring set constructed of stainless steel with ends flat and slotted to accept metal bands. Spring size determined by manufacturer for application.

B. Insulation Pins and Hangers:

1. Capacitor-Discharge-Weld Pins: Copper- or zinc-coated steel pin, fully annealed for capacitor-discharge welding, [0.106-inch- (2.6-mm-)] [0.135-inch- (3.5-mm-)] diameter shank, length to suit depth of insulation indicated.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

a. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

1) AGM Industries, Inc.

2) Gemco.

3) Hardcast, Inc.

4) Midwest Fasteners, Inc.

5) Nelson Stud Welding.
6) <Insert manufacturer's name>.
2. Cupped-Head, Capacitor-Discharge-Weld Pins: Copper- or zinc-coated steel pin, fully annealed for capacitor-discharge welding, [0.106-inch- (2.6-mm-)] [0.135-inch- (3.5-mm-)] diameter shank, length to suit depth of insulation indicated with integral 1-1/2-inch (38-mm) galvanized carbon-steel washer.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

a. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

1) AGM Industries, Inc.

2) CL WARD & Family Inc.

3) Gemco.

4) Hardcast, Inc.

5) Midwest Fasteners, Inc.

6) Nelson Stud Welding.
7) <Insert manufacturer's name>.
3. Metal, Adhesively Attached, Perforated-Base Insulation Hangers: Baseplate welded to projecting spindle that is capable of holding insulation, of thickness indicated, securely in position indicated when self-locking washer is in place. Comply with the following requirements:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

a. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

1) AGM Industries, Inc.

2) Gemco.

3) Midwest Fasteners, Inc.
4) <Insert manufacturer's name>.
b. Baseplate: Perforated, galvanized carbon-steel sheet, 0.030 inch (0.76 mm) thick by 2 inches (50 mm) square.

c. Spindle: [Copper- or zinc-coated, low-carbon steel] [Aluminum] [Stainless steel], fully annealed, 0.106-inch- (2.6-mm-) diameter shank, length to suit depth of insulation indicated.

d. Adhesive: Recommended by hanger manufacturer. Product with demonstrated capability to bond insulation hanger securely to substrates indicated without damaging insulation, hangers, and substrates.

4. Nonmetal, Adhesively Attached, Perforated-Base Insulation Hangers: Baseplate fastened to projecting spindle that is capable of holding insulation, of thickness indicated, securely in position indicated when self-locking washer is in place. Comply with the following requirements:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

a. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

1) Gemco.

2) Midwest Fasteners, Inc.
3) <Insert manufacturer's name>.
b. Baseplate: Perforated, nylon sheet, 0.030 inch (0.76 mm) thick by 1-1/2 inches (38 mm) in diameter.

c. Spindle: Nylon, 0.106-inch- (2.6-mm-) diameter shank, length to suit depth of insulation indicated, up to 2-1/2 inches (63 mm).

d. Adhesive: Recommended by hanger manufacturer. Product with demonstrated capability to bond insulation hanger securely to substrates indicated without damaging insulation, hangers, and substrates.

5. Self-Sticking-Base Insulation Hangers: Baseplate welded to projecting spindle that is capable of holding insulation, of thickness indicated, securely in position indicated when self-locking washer is in place. Comply with the following requirements:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

a. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

1) AGM Industries, Inc.

2) Gemco.

3) Hardcast, Inc.

4) Midwest Fasteners, Inc.
5) <Insert manufacturer's name>.
b. Baseplate: Galvanized carbon-steel sheet, 0.030 inch (0.76 mm) thick by 2 inches (50 mm) square.

c. Spindle: [Copper- or zinc-coated, low-carbon steel] [Aluminum] [Stainless steel], fully annealed, 0.106-inch- (2.6-mm-) diameter shank, length to suit depth of insulation indicated.

d. Adhesive-backed base with a peel-off protective cover.

6. Insulation-Retaining Washers: Self-locking washers formed from 0.016-inch- (0.41-mm-) thick, [galvanized-steel] [aluminum] [stainless steel] sheet, with beveled edge sized as required to hold insulation securely in place but not less than 1-1/2 inches (38 mm) in diameter.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

a. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

1) AGM Industries, Inc.

2) Gemco.

3) Hardcast, Inc.

4) Midwest Fasteners, Inc.

5) Nelson Stud Welding.
6) <Insert manufacturer's name>.
b. Protect ends with capped self-locking washers incorporating a spring steel insert to ensure permanent retention of cap in exposed locations.

7. Nonmetal Insulation-Retaining Washers: Self-locking washers formed from 0.016-inch- (0.41-mm-) thick nylon sheet, with beveled edge sized as required to hold insulation securely in place but not less than 1-1/2 inches (38 mm) in diameter.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

a. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

1) Gemco.

2) Midwest Fasteners, Inc.
3) <Insert manufacturer's name>.
C. Staples: Outward-clinching insulation staples, nominal 3/4-inch- (19-mm-) wide, stainless steel or Monel.

In paragraph below, stainless steel is the most common wire used and is best suited for all applications.

D. Wire: [0.080-inch (2.0-mm) nickel-copper alloy] [0.062-inch (1.6-mm) soft-annealed, stainless steel] [0.062-inch (1.6-mm) soft-annealed, galvanized steel].

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by the following:

a. C & F Wire.
b. <Insert manufacturer's name>.
2.13 CORNER ANGLES

A. PVC Corner Angles: [30 mils (0.8 mm)] <Insert dimension> thick, minimum 1 by 1 inch (25 by 25 mm), PVC in accordance with ASTM D1784, Class 16354-C. White or color-coded to match adjacent surface.

B. Aluminum Corner Angles: [0.040 inch (1.0 mm)] <Insert dimension> thick, minimum 1 by 1 inch (25 by 25 mm), aluminum in accordance with ASTM B209 (ASTM B209M), Alloy 3003, 3005, 3105, or 5005; Temper H-14.

C. Stainless Steel Corner Angles: [0.024 inch (0.61 mm)] <Insert dimension> thick, minimum 1 by 1 inch (25 by 25 mm), stainless steel in accordance with ASTM A167 or ASTM A240/A240M, [Type 304] [or] [Type 316].

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine substrates and conditions for compliance with requirements for installation tolerances and other conditions affecting performance of insulation application.

1. Verify that systems to be insulated have been tested and are free of defects.

2. Verify that surfaces to be insulated are clean and dry.

B. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 PREPARATION

A. Surface Preparation: Clean and dry surfaces to receive insulation. Remove materials that will adversely affect insulation application.

3.3 GENERAL INSTALLATION REQUIREMENTS

A. Install insulation materials, accessories, and finishes with smooth, straight, and even surfaces; free of voids throughout the length of ducts and fittings.

B. Install insulation materials, vapor barriers or retarders, jackets, and thicknesses required for each item of duct system as specified in insulation system schedules.

C. Install accessories compatible with insulation materials and suitable for the service. Install accessories that do not corrode, soften, or otherwise attack insulation or jacket in either wet or dry state.

D. Install insulation with longitudinal seams at top and bottom of horizontal runs.

E. Install multiple layers of insulation with longitudinal and end seams staggered.

F. Keep insulation materials dry during application and finishing.

G. Install insulation with tight longitudinal seams and end joints. Bond seams and joints with adhesive recommended by insulation material manufacturer.

H. Install insulation with least number of joints practical.

I. Where vapor barrier is indicated, seal joints, seams, and penetrations in insulation at hangers, supports, anchors, and other projections with vapor-barrier mastic.

1. Install insulation continuously through hangers and around anchor attachments.

2. For insulation application where vapor barriers are indicated, extend insulation on anchor legs from point of attachment to supported item to point of attachment to structure. Taper and seal ends at attachment to structure with vapor-barrier mastic.

3. Install insert materials and install insulation to tightly join the insert. Seal insulation to insulation inserts with adhesive or sealing compound recommended by insulation material manufacturer.

J. Apply adhesives, mastics, and sealants at manufacturer's recommended coverage rate and wet and dry film thicknesses.

K. Install insulation with factory-applied jackets as follows:

1. Draw jacket tight and smooth.

2. Cover circumferential joints with 3-inch- (75-mm-) wide strips, of same material as insulation jacket. Secure strips with adhesive and outward clinching staples along both edges of strip, spaced 4 inches (100 mm) o.c.

3. Overlap jacket longitudinal seams at least 1-1/2 inches (38 mm). Clean and dry surface to receive self-sealing lap. Staple laps with outward clinching staples along edge at [2 inches (50 mm)] [4 inches (100 mm)] o.c.

a. For below ambient services, apply vapor-barrier mastic over staples.

4. Cover joints and seams with tape, in accordance with insulation material manufacturer's written instructions, to maintain vapor seal.

5. Where vapor barriers are indicated, apply vapor-barrier mastic on seams and joints and at ends adjacent to duct flanges and fittings.

L. Cut insulation in a manner to avoid compressing insulation more than 75 percent of its nominal thickness.

M. Finish installation with systems at operating conditions. Repair joint separations and cracking due to thermal movement.

N. Repair damaged insulation facings by applying same facing material over damaged areas. Extend patches at least 4 inches (100 mm) beyond damaged areas. Adhere, staple, and seal patches similar to butt joints.

3.4 PENETRATIONS

A. Insulation Installation at Roof Penetrations: Install insulation continuously through roof penetrations.

1. Seal penetrations with flashing sealant.

2. For applications requiring only indoor insulation, terminate insulation above roof surface and seal with joint sealant. For applications requiring indoor and outdoor insulation, install insulation for outdoor applications tightly joined to indoor insulation ends. Seal joint with joint sealant.

3. Extend jacket of outdoor insulation outside roof flashing at least 2 inches (50 mm) below top of roof flashing.

4. Seal jacket to roof flashing with flashing sealant.

B. Insulation Installation at Aboveground Exterior Wall Penetrations: Install insulation continuously through wall penetrations.

1. Seal penetrations with flashing sealant.

2. For applications requiring only indoor insulation, terminate insulation inside wall surface and seal with joint sealant. For applications requiring indoor and outdoor insulation, install insulation for outdoor applications tightly joined to indoor insulation ends. Seal joint with joint sealant.

3. Extend jacket of outdoor insulation outside wall flashing and overlap wall flashing at least 2 inches (50 mm).

4. Seal jacket to wall flashing with flashing sealant.

C. Insulation Installation at Interior Wall and Partition Penetrations (That Are Not Fire Rated): Install insulation continuously through walls and partitions.

D. Insulation Installation at Fire-Rated Wall and Partition Penetrations: Terminate insulation at fire damper sleeves for fire-rated wall and partition penetrations. Externally insulate damper sleeves to match adjacent insulation and overlap duct insulation at least 2 inches (50 mm).

1. Comply with requirements in Section 078413 "Penetration Firestopping."

E. Insulation Installation at Floor Penetrations:

1. Duct: For penetrations through fire-rated assemblies, terminate insulation at fire damper sleeves and externally insulate damper sleeve beyond floor to match adjacent duct insulation. Overlap damper sleeve and duct insulation at least 2 inches (50 mm).

2. Seal penetrations through fire-rated assemblies. Comply with requirements in Section 078413 "Penetration Firestopping."

3.5 INSTALLATION OF FLEXIBLE ELASTOMERIC INSULATION

A. Seal longitudinal seams and end joints with manufacturer's recommended adhesive to eliminate openings in insulation that allow passage of air to surface being insulated.

3.6 INSTALLATION OF MINERAL-FIBER INSULATION

A. Blanket Insulation Installation on Ducts and Plenums: Secure with adhesive and insulation pins.

In first subparagraph below, many manufacturers do not recommend 100 percent coverage of adhesive because of the effect on the overall insulation system's fire-performance characteristics. Verify application coverage recommendations with insulation manufacturer.

1. Apply adhesives in accordance with manufacturer's recommended coverage rates per unit area, for [100] [50] <Insert number> percent coverage of duct and plenum surfaces.

Revise first subparagraph below to allow adhesive to be omitted from top surface of horizontal rectangular ducts.

2. Apply adhesive to entire circumference of ducts and to all surfaces of fittings and transitions.

3. Install either capacitor-discharge-weld pins and speed washers or cupped-head, capacitor-discharge-weld pins on sides and bottom of horizontal ducts and sides of vertical ducts as follows:

a. On duct sides with dimensions 18 inches (450 mm) and smaller, place pins along longitudinal centerline of duct. Space 3 inches (75 mm) maximum from insulation end joints, and 16 inches (400 mm) o.c.

b. On duct sides with dimensions larger than 18 inches (450 mm), place pins 16 inches (400 mm) o.c. each way, and 3 inches (75 mm) maximum from insulation joints. Install additional pins to hold insulation tightly against surface at cross bracing.

c. Pins may be omitted from top surface of horizontal, rectangular ducts and plenums.

d. Do not overcompress insulation during installation.

e. Impale insulation over pins and attach speed washers.

f. Cut excess portion of pins extending beyond speed washers or bend parallel with insulation surface. Cover exposed pins and washers with tape matching insulation facing.

4. For ducts and plenums with surface temperatures below ambient, install a continuous unbroken vapor barrier. Create a facing lap for longitudinal seams and end joints with insulation by removing 2 inches (50 mm) from one edge and one end of insulation segment. Secure laps to adjacent insulation section with 1/2-inch (13-mm) outward-clinching staples, 1 inch (25 mm) o.c. Install vapor barrier consisting of factory- or field-applied jacket, adhesive, vapor-barrier mastic, and sealant at joints, seams, and protrusions.

a. Repair punctures, tears, and penetrations with tape or mastic to maintain vapor-barrier seal.

b. Install vapor stops for ductwork and plenums operating below 50 deg F (10 deg C) at 18-foot (5.5-m) intervals. Vapor stops shall consist of vapor-barrier mastic applied in a Z-shaped pattern over insulation face, along butt end of insulation, and over the surface. Cover insulation face and surface to be insulated a width equal to two times the insulation thickness, but not less than 3 inches (75 mm).

5. Overlap unfaced blankets a minimum of 2 inches (50 mm) on longitudinal seams and end joints. At end joints, secure with steel bands spaced a maximum of 18 inches (450 mm) o.c.

6. Install insulation on rectangular duct elbows and transitions with a full insulation section for each surface. Install insulation on round and flat-oval duct elbows with individually mitered gores cut to fit the elbow.

7. Insulate duct stiffeners, hangers, and flanges that protrude beyond insulation surface with 6-inch- (150-mm-) wide strips of same material used to insulate duct. Secure on alternating sides of stiffener, hanger, and flange with pins spaced 6 inches (150 mm) o.c.

B. Board Insulation Installation on Ducts and Plenums: Secure with adhesive and insulation pins.

In first subparagraph below, many manufacturers do not recommend 100 percent coverage of adhesive because of the effect on the overall insulation system's fire-performance characteristics. Verify application coverage recommendations with insulation manufacturer.

1. Apply adhesives in accordance with manufacturer's recommended coverage rates per unit area, for [100] [50] <Insert number> percent coverage of duct and plenum surfaces.

Revise first subparagraph below to allow adhesive to be omitted from top surface of horizontal rectangular ducts.

2. Apply adhesive to entire circumference of ducts and to all surfaces of fittings and transitions.

3. Install either capacitor-discharge-weld pins and speed washers or cupped-head, capacitor-discharge-weld pins on sides and bottom of horizontal ducts and sides of vertical ducts as follows:

a. On duct sides with dimensions 18 inches (450 mm) and smaller, place pins along longitudinal centerline of duct. Space 3 inches (75 mm) maximum from insulation end joints, and 16 inches (400 mm) o.c.

b. On duct sides with dimensions larger than 18 inches (450 mm), space pins 16 inches (400 mm) o.c. each way, and 3 inches (75 mm) maximum from insulation joints. Install additional pins to hold insulation tightly against surface at cross bracing.

c. Pins may be omitted from top surface of horizontal, rectangular ducts and plenums.

d. Do not overcompress insulation during installation.

e. Cut excess portion of pins extending beyond speed washers or bend parallel with insulation surface. Cover exposed pins and washers with tape matching insulation facing.

4. For ducts and plenums with surface temperatures below ambient, install a continuous unbroken vapor barrier. Create a facing lap for longitudinal seams and end joints with insulation by removing 2 inches (50 mm) from one edge and one end of insulation segment. Secure laps to adjacent insulation section with 1/2-inch (13-mm) outward-clinching staples, 1 inch (25 mm) o.c. Install vapor barrier consisting of factory- or field-applied jacket, adhesive, vapor-barrier mastic, and sealant at joints, seams, and protrusions.

a. Repair punctures, tears, and penetrations with tape or mastic to maintain vapor-barrier seal.

b. Install vapor stops for ductwork and plenums operating below 50 deg F (10 deg C) at 18-foot (5.5-m) intervals. Vapor stops shall consist of vapor-barrier mastic applied in a Z-shaped pattern over insulation face, along butt end of insulation, and over the surface. Cover insulation face and surface to be insulated a width equal to two times the insulation thickness, but not less than 3 inches (75 mm).

5. Install insulation on rectangular duct elbows and transitions with a full insulation section for each surface. Groove and score insulation to fit as closely as possible to outside and inside radius of elbows. Install insulation on round and flat-oval duct elbows with individually mitered gores cut to fit the elbow.

6. Insulate duct stiffeners, hangers, and flanges that protrude beyond insulation surface with 6-inch- (150-mm-) wide strips of same material used to insulate duct. Secure on alternating sides of stiffener, hanger, and flange with pins spaced 6 inches (150 mm) o.c.

3.7 FIELD-APPLIED JACKET INSTALLATION

A. Where glass-cloth jackets are indicated, install directly over bare insulation or insulation with factory-applied jackets.

1. Draw jacket smooth and tight to surface with 2-inch (50-mm) overlap at seams and joints.

2. Embed glass cloth between two 0.062-inch- (1.6-mm-) thick coats of lagging adhesive.

3. Completely encapsulate insulation with coating, leaving no exposed insulation.

B. Where FSK jackets are indicated, install as follows:

1. Draw jacket material smooth and tight.

2. Install lap or joint strips with same material as jacket.

3. Secure jacket to insulation with manufacturer's recommended adhesive.

4. Install jacket with 1-1/2-inch (38-mm) laps at longitudinal seams and 3-inch- (75-mm-) wide joint strips at end joints.

5. Seal openings, punctures, and breaks in vapor-retarder jackets and exposed insulation with vapor-barrier mastic.

C. Where PVC jackets are indicated, install with 1-inch (25-mm) overlap at longitudinal seams and end joints; for horizontal applications, install with longitudinal seams along top and bottom of tanks and vessels. Seal with manufacturer's recommended adhesive.

1. Apply two continuous beads of adhesive to seams and joints, one bead under lap and the finish bead along seam and joint edge.

D. Where metal jackets are indicated, install with 2-inch (50-mm) overlap at longitudinal seams and end joints. Overlap longitudinal seams arranged to shed water. Seal end joints with weatherproof sealant recommended by insulation manufacturer. Secure jacket with stainless steel bands 12 inches (300 mm) o.c. and at end joints.

3.8 FIRE-RATED INSULATION SYSTEM INSTALLATION

A. Where fire-rated insulation system is indicated, secure system to ducts and duct hangers and supports to maintain a continuous fire rating.

B. Insulate duct access panels and doors to achieve same fire rating as duct.

C. Install firestopping at penetrations through fire-rated assemblies. Fire-stop systems are specified in Section 078413 "Penetration Firestopping."

3.9 FINISHES

Coordinate first paragraph below with Section 099113 "Exterior Painting" and Section 099123 "Interior Painting." If PVC jackets are specified, consult jacket manufacturers to determine suitable paint products and revise painting Sections to suit Project.

A. Insulation with ASJ, Glass-Cloth, or Other Paintable Jacket Material: Paint jacket with paint system identified below and as specified in Section 099113 "Exterior Painting" and Section 099123 "Interior Painting."

Retain paint system in subparagraphs below for a flat, latex-emulsion size over insulation covering an exterior that is subject to normal use and moderate environments.

1. Flat Acrylic Finish: [Two] <Insert number> finish coats over a primer that is compatible with jacket material and finish coat paint. Add fungicidal agent to render fabric mildew proof.

a. Finish Coat Material: Interior, flat, latex-emulsion size.

B. Flexible Elastomeric Thermal Insulation: After adhesive has fully cured, apply two coats of insulation manufacturer's recommended protective coating.

C. Color: Final color as selected by Architect. Vary first and second coats to allow visual inspection of the completed Work.

D. Do not field paint aluminum or stainless steel jackets.

3.10 FIELD QUALITY CONTROL

Inspections in this article are destructive. Retain if workmanship quality is an important requirement. Architect should be prepared to reject all work if defective work is discovered in sample inspection.

Retain one of first two paragraphs below to identify who shall perform tests and inspections. If retaining second option in first paragraph, or if retaining second paragraph, retain "Field quality-control reports" Paragraph in "Informational Submittals" Article.

A. Testing Agency: [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

Retain first paragraph below to require Contractor to perform tests and inspections.

B. Perform tests and inspections.

Retain first paragraph below to describe tests and inspections to be performed.

C. Tests and Inspections:

1. Inspect ductwork, randomly selected by Architect, by removing field-applied jacket and insulation in layers in reverse order of their installation. Extent of inspection shall be limited to [one] <Insert number> location(s) for each duct system defined in the "Duct Insulation Schedule, General" Article.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

D. All insulation applications will be considered defective Work if sample inspection reveals noncompliance with requirements.

Materials and thicknesses in schedules below are for single-layer applications. If multilayer applications are needed, insert additional requirements.

3.11 DUCT INSULATION SCHEDULE, GENERAL

A. Plenums and Ducts Requiring Insulation:

1. Indoor, concealed supply and outdoor air.

2. Indoor, exposed supply and outdoor air.

3. Indoor, concealed return located in unconditioned space.

4. Indoor, exposed return located in unconditioned space.

5. Indoor, concealed, Type I, commercial, kitchen hood exhaust.

6. Indoor, exposed, Type I, commercial, kitchen hood exhaust.

7. Indoor, concealed oven and warewash exhaust.

8. Indoor, exposed oven and warewash exhaust.

9. Indoor, concealed exhaust between isolation damper and penetration of building exterior.

10. Indoor, exposed exhaust between isolation damper and penetration of building exterior.

11. Outdoor, concealed supply and return.

12. Outdoor, exposed supply and return.

B. Items Not Insulated:

1. Fibrous-glass ducts.

2. Metal ducts with duct liner of sufficient thickness to comply with energy code and ASHRAE/IESNA 90.1.

3. Factory-insulated flexible ducts.

4. Factory-insulated plenums and casings.

5. Flexible connectors.

6. Vibration-control devices.

7. Factory-insulated access panels and doors.

Duct and plenum insulation schedules in first two articles below specify commonly used insulation materials and thicknesses for each service type. LEED Prerequisite EA 2 requires that duct insulation R-value comply with ASHRAE/IESNA 90.1 tables titled "Minimum Duct Insulation R-Value, Cooling and Heating Only Supply Ducts and Return Ducts" and "Minimum Duct Insulation R-Value, Combined Heating and Cooling Supply Ducts and Return Ducts." Not all materials and thicknesses may be suitable for a specific project. Revise to suit Project after considering all parameters that impact selection. Do not duplicate requirements inserted in "Insulation Materials" Article. See the Evaluations for more information and guidance.

Flexible elastomeric and polyolefin thicknesses are limited to 1 inch (25 mm) to meet a flame-spread index of 25 and a smoke-developed index of 50. Condensation control and energy efficiency are limited by thickness.

Consider the exposure of installed insulation to damage. Concealed applications have less risk than exposed.

3.12 INDOOR DUCT AND PLENUM INSULATION SCHEDULE

See the Insulation Evaluation tables in the Evaluations for rankings of different insulation types for different service ranges.

Retain "one of" option in paragraphs below to allow Contractor to select piping materials from those retained.

A. Concealed, round and flat-oval, supply-air duct insulation shall be[ one of] the following:

Retain one or more of four subparagraphs below.

1. Flexible Elastomeric: [1 inch (25 mm)] <Insert dimension> thick.

2. Mineral-Fiber Blanket: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

3. Mineral-Fiber Board: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

4. Polyolefin: [1 inch (25 mm)] <Insert dimension> thick.

B. Concealed, round and flat-oval, return-air duct insulation shall be[ one of] the following:

Retain one or more of four subparagraphs below.

1. Flexible Elastomeric: [1 inch (25 mm)] <Insert dimension> thick.

2. Mineral-Fiber Blanket: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

3. Mineral-Fiber Board: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

4. Polyolefin: [1 inch (25 mm)] <Insert dimension> thick.

C. Concealed, round and flat-oval, outdoor-air duct insulation shall be[ one of] the following:

Retain one or more of four subparagraphs below.

1. Flexible Elastomeric: [1 inch (25 mm)] <Insert dimension> thick.

2. Mineral-Fiber Blanket: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

3. Mineral-Fiber Board: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

4. Polyolefin: [1 inch (25 mm)] <Insert dimension> thick.

D. Concealed, round and flat-oval, exhaust-air duct insulation shall be[ one of] the following:

Retain one or more of four subparagraphs below.

1. Flexible Elastomeric: [1 inch (25 mm)] <Insert dimension> thick.

2. Mineral-Fiber Blanket: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

3. Mineral-Fiber Board: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

4. Polyolefin: [1 inch (25 mm)] <Insert dimension> thick.

E. Concealed, rectangular, supply-air duct insulation shall be[ one of] the following:

Retain one or more of four subparagraphs below.

1. Flexible Elastomeric: [1 inch (25 mm)] <Insert dimension> thick.

2. Mineral-Fiber Blanket: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

3. Mineral-Fiber Board: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

4. Polyolefin: [1 inch (25 mm)] <Insert dimension> thick.

F. Concealed, rectangular, return-air duct insulation shall be[ one of] the following:

Retain one or more of four subparagraphs below.

1. Flexible Elastomeric: [1 inch (25 mm)] <Insert dimension> thick.

2. Mineral-Fiber Blanket: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

3. Mineral-Fiber Board: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

4. Polyolefin: [1 inch (25 mm)] <Insert dimension> thick.

G. Concealed, rectangular, outdoor-air duct insulation shall be[ one of] the following:

Retain one or more of four subparagraphs below.

1. Flexible Elastomeric: [1 inch (25 mm)] <Insert dimension> thick.

2. Mineral-Fiber Blanket: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

3. Mineral-Fiber Board: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

4. Polyolefin: [1 inch (25 mm)] <Insert dimension> thick.

H. Concealed, rectangular, exhaust-air duct insulation between isolation damper and penetration of building exterior shall be[ one of] the following:

Retain one or more of four subparagraphs below.

1. Flexible Elastomeric: [1 inch (25 mm)] <Insert dimension> thick.

2. Mineral-Fiber Blanket: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

3. Mineral-Fiber Board: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

4. Polyolefin: [1 inch (25 mm)] <Insert dimension> thick.

I. Concealed, Type I, Commercial, Kitchen Hood Exhaust Duct and Plenum Insulation: Fire-rated [blanket] [or] [board]; thickness as required to achieve 2-hour fire rating.

J. Concealed, supply-air plenum insulation shall be[ one of] the following:

Retain one or more of four subparagraphs below.

1. Flexible Elastomeric: [1 inch (25 mm)] <Insert dimension> thick.

2. Mineral-Fiber Blanket: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

3. Mineral-Fiber Board: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

4. Polyolefin: [1 inch (25 mm)] <Insert dimension> thick.

K. Concealed, return-air plenum insulation shall be[ one of] the following:

Retain one or more of four subparagraphs below.

1. Flexible Elastomeric: [1 inch (25 mm)] <Insert dimension> thick.

2. Mineral-Fiber Blanket: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

3. Mineral-Fiber Board: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

4. Polyolefin: [1 inch (25 mm)] <Insert dimension> thick.

L. Concealed, outdoor-air plenum insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

1. Mineral-Fiber Blanket: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

2. Mineral-Fiber Board: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

M. Concealed, exhaust-air plenum insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

1. Mineral-Fiber Blanket: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

2. Mineral-Fiber Board: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

N. Exposed, round and flat-oval, supply-air duct insulation shall be[ one of] the following:

Retain one or more of five subparagraphs below.

1. Flexible Elastomeric: [1 inch (25 mm)] <Insert dimension> thick.

2. Mineral-Fiber Blanket: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

3. Mineral-Fiber Board: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

4. Mineral-Fiber Pipe and Tank: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick.

5. Polyolefin: [1 inch (25 mm)] <Insert dimension> thick.

O. Exposed, round and flat-oval, return-air duct insulation shall be[ one of] the following:

Retain one or more of five subparagraphs below.

1. Flexible Elastomeric: [1 inch (25 mm)] <Insert dimension> thick.

2. Mineral-Fiber Blanket: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

3. Mineral-Fiber Board: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

4. Mineral-Fiber Pipe and Tank: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick.

5. Polyolefin: [1 inch (25 mm)] <Insert dimension> thick.

P. Exposed, round and flat-oval, outdoor-air duct insulation shall be[ one of] the following:

Retain one or more of five subparagraphs below.

1. Flexible Elastomeric: [1 inch (25 mm)] <Insert dimension> thick.

2. Mineral-Fiber Blanket: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

3. Mineral-Fiber Board: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

4. Mineral-Fiber Pipe and Tank: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick.

5. Polyolefin: [1 inch (25 mm)] <Insert dimension> thick.

Q. Exposed, round and flat-oval, exhaust-air duct insulation shall be[ one of] the following:

Retain one or more of five subparagraphs below.

1. Flexible Elastomeric: [1 inch (25 mm)] <Insert dimension> thick.

2. Mineral-Fiber Blanket: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

3. Mineral-Fiber Board: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

4. Mineral-Fiber Pipe and Tank: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick.

5. Polyolefin: [1 inch (25 mm)] <Insert dimension> thick.

R. Exposed, rectangular, supply-air duct insulation shall be[ one of] the following:

Retain one or more of four subparagraphs below.

1. Flexible Elastomeric: [1 inch (25 mm)] <Insert dimension> thick.

2. Mineral-Fiber Blanket: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

3. Mineral-Fiber Board: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96 kg/cu. m)] nominal density.

4. Polyolefin: [1 inch (25 mm)] <Insert dimension> thick.

S. Exposed, rectangular, return-air duct insulation shall be[ one of] the following:

Retain one or more of four subparagraphs below.

1. Flexible Elastomeric: [1 inch (25 mm)] <Insert dimension> thick.

2. Mineral-Fiber Blanket: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

3. Mineral-Fiber Board: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

4. Polyolefin: [1 inch (25 mm)] <Insert dimension> thick.

T. Exposed, rectangular, outdoor-air duct insulation shall be[ one of] the following:

Retain one or more of four subparagraphs below.

1. Flexible Elastomeric: [1 inch (25 mm)] <Insert dimension> thick.

2. Mineral-Fiber Blanket: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

3. Mineral-Fiber Board: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

4. Polyolefin: [1 inch (25 mm)] <Insert dimension> thick.

U. Exposed, rectangular, exhaust-air duct insulation shall be[ one of] the following:

Retain one or more of four subparagraphs below.

1. Flexible Elastomeric: [1 inch (25 mm)] <Insert dimension> thick.

2. Mineral-Fiber Blanket: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

3. Mineral-Fiber Board: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

4. Polyolefin: [1 inch (25 mm)] <Insert dimension> thick.

V. Exposed, Type I, Commercial, Kitchen Hood Exhaust Duct and Plenum Insulation: Fire-rated [blanket] [or] [board]; thickness as required to achieve 2-hour fire rating.

W. Exposed, supply-air plenum insulation shall be[ one of] the following:

Retain one or more of four subparagraphs below.

1. Flexible Elastomeric: [1 inch (25 mm)] <Insert dimension> thick.

2. Mineral-Fiber Blanket: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

3. Mineral-Fiber Board: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

4. Polyolefin: [1 inch (25 mm)] <Insert dimension> thick.

X. Exposed, return-air plenum insulation shall be[ one of] the following:

Retain one or more of four subparagraphs below.

1. Flexible Elastomeric: [1 inch (25 mm)] <Insert dimension> thick.

2. Mineral-Fiber Blanket: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

3. Mineral-Fiber Board: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

4. Polyolefin: [1 inch (25 mm)] <Insert dimension> thick.

Y. Exposed, outdoor-air plenum insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

1. Mineral-Fiber Blanket: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

2. Mineral-Fiber Board: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

Z. Exposed, exhaust-air plenum insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

1. Mineral-Fiber Blanket: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

2. Mineral-Fiber Board: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

3.13 ABOVEGROUND, OUTDOOR DUCT AND PLENUM INSULATION SCHEDULE

See the Insulation Evaluation tables in the Evaluations for rankings of different insulation types for different service ranges.

Retain "one of" option in paragraphs below to allow Contractor to select piping materials from those retained.

To comply with ASHRAE/IESNA 90.1, insulation should have an R-value of 8 or higher.

A. Insulation materials and thicknesses are identified below. If more than one material is listed for a duct system, selection from materials listed is Contractor's option.

B. Concealed, round and flat-oval, supply-air duct insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

1. Mineral-Fiber Blanket: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

2. Mineral-Fiber Board: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

C. Concealed, round and flat-oval, return-air duct insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

1. Mineral-Fiber Blanket: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

2. Mineral-Fiber Board: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

D. Concealed, round and flat-oval, outdoor-air duct insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

1. Mineral-Fiber Blanket: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

2. Mineral-Fiber Board: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

E. Concealed, rectangular, supply-air duct insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

1. Mineral-Fiber Blanket: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

2. Mineral-Fiber Board: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

F. Concealed, rectangular, return-air duct insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

1. Mineral-Fiber Blanket: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

2. Mineral-Fiber Board: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

G. Concealed, supply-air plenum insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

1. Mineral-Fiber Blanket: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

2. Mineral-Fiber Board: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

H. Concealed, return-air plenum insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

1. Mineral-Fiber Blanket: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

2. Mineral-Fiber Board: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

I. Exposed, round and flat-oval, supply-air duct insulation shall be[ one of] the following:

Retain one or more of three subparagraphs below.

1. Mineral-Fiber Blanket: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

2. Mineral-Fiber Board: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

3. Mineral-Fiber Pipe and Tank: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick.

J. Exposed, round and flat-oval, return-air duct insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

1. Mineral-Fiber Blanket: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

2. Mineral-Fiber Board: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

K. Exposed, rectangular, supply-air duct insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

1. Mineral-Fiber Blanket: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

2. Mineral-Fiber Board: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

L. Exposed, rectangular, return-air duct insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

1. Mineral-Fiber Blanket: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

2. Mineral-Fiber Board: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

M. Exposed, supply-air plenum insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

1. Mineral-Fiber Blanket: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

2. Mineral-Fiber Board: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

N. Exposed, return-air plenum insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

1. Mineral-Fiber Blanket: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

2. Mineral-Fiber Board: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

3.14 INDOOR, FIELD-APPLIED JACKET SCHEDULE

Possible variations of jackets by location are endless. This article specifies locations in two broad categories: concealed and exposed. Revise if additional delineation is necessary.

A. Install jacket over insulation material. For insulation with factory-applied jacket, install the field-applied jacket over the factory-applied jacket.

B. If more than one material is listed, selection from materials listed is Contractor's option.

C. Ducts and Plenums, Concealed:

Retain one of six subparagraphs below.

1. None.

2. [PVC] [PVC, Color-Coded by System]: [20 mils (0.5 mm)] [30 mils (0.8 mm)] thick.

3. Aluminum, [Smooth] [Corrugated] [Stucco Embossed]: [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] [0.040 inch (1.0 mm)] thick.

4. Painted Aluminum, [Smooth] [Corrugated] [Stucco Embossed]: [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] thick.

5. Stainless Steel, [Type 304] [or] [Type 316], [Smooth 2B Finish] [Corrugated] [Stucco Embossed]: [0.010 inch (0.25 mm)] [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] thick.

6. <Insert jacket type>.

D. Ducts and Plenums, Exposed:

Retain one of six subparagraphs below.

1. None.

2. [PVC] [PVC, Color-Coded by System]: [20 mils (0.5 mm)] [30 mils (0.8 mm)] thick.

3. Aluminum, [Smooth] [Corrugated] [Stucco Embossed]: [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] [0.040 inch (1.0 mm)] thick.

4. Painted Aluminum, [Smooth] [Corrugated] [Stucco Embossed]: [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] thick.

5. Stainless Steel, [Type 304] [or] [Type 316], [Smooth 2B Finish] [Corrugated] [Stucco Embossed]: [0.010 inch (0.25 mm)] [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] thick.

6. <Insert jacket type>.

3.15 OUTDOOR, FIELD-APPLIED JACKET SCHEDULE

Possible variations of jackets by location are endless. This article specifies locations in two broad categories: concealed and exposed. Revise if additional delineation is necessary.

30-mil (0.8-mm) or heavier PVC is recommended for outdoor applications. 40-mil (1.0-mm) PVC does not meet a flame-spread index of 25 and a smoke-developed index of 50; however, a flame-spread or smoke-developed index is not a requirement for outdoor applications.

0.024-inch (0.61-mm) or heavier aluminum is recommended for outdoor applications.

Painted aluminum increases surface emissivity and provides added chemical resistance. See the Evaluations for discussion of emissivity.

0.016-inch (0.41-mm) or heavier stainless steel is recommended for outdoor applications.

Z-shaped locking seam is recommended for metal jackets located in unprotected applications that are exposed to severe weather.

A. Install jacket over insulation material. For insulation with factory-applied jacket, install the field-applied jacket over the factory-applied jacket.

B. If more than one material is listed, selection from materials listed is Contractor's option.

C. Ducts and Plenums, Concealed:

Retain one of six subparagraphs below.

1. None.

2. [PVC] [PVC, Color-Coded by System]: [20 mils (0.5 mm)] [30 mils (0.8 mm)] thick.

3. Aluminum, [Smooth] [Corrugated] [Stucco Embossed]: [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] [0.040 inch (1.0 mm)] thick.

4. Painted Aluminum, [Smooth] [Corrugated] [Stucco Embossed]: [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] thick.

5. Stainless Steel, [Type 304] [or] [Type 316], [Smooth 2B Finish] [Corrugated] [Stucco Embossed]: [0.010 inch (0.25 mm)] [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] thick.

6. <Insert jacket type>.

D. Ducts and Plenums, Exposed, up to 48 Inches (1200 mm) in Diameter or with Flat Surfaces up to 72 Inches (1800 mm):

Retain one of four subparagraphs below.

1. Aluminum, [Smooth] [Corrugated] [Stucco Embossed]: [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] [0.040 inch (1.0 mm)] thick.

2. Painted Aluminum, [Smooth] [Corrugated] [Stucco Embossed]: [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] thick.

3. Stainless Steel, [Type 304] [or] [Type 316], [Smooth 2B Finish] [Corrugated] [Stucco Embossed]: [0.010 inch (0.25 mm)] [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] thick.

4. <Insert jacket type>.

E. Ducts and Plenums, Exposed, Larger Than 48 Inches (1200 mm) in Diameter or with Flat Surfaces Larger Than 72 Inches (1800 mm):

Retain one of three subparagraphs below.

1. [Painted ]Aluminum, [Smooth] [Stucco Embossed] with [1-1/4-Inch- (32-mm-) Deep Corrugations] [2-1/2-Inch- (65-mm-) Deep Corrugations] [4-by-1-Inch (100-by-25-mm) Box Ribs]: [0.032 inch (0.81 mm)] [0.040 inch (1.0 mm)] thick.

2. Stainless Steel, [Type 304] [or] [Type 316], [Smooth] [Stucco Embossed], with [1-1/4-Inch- (32-mm-) Deep Corrugations] [2-1/2-Inch- (65-mm-) Deep Corrugations] [4-by-1-Inch (100-by-25-mm) Box Ribs]: [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] thick.

3. <Insert jacket type>.

END OF SECTION 230713

	DUCT INSULATION
	230713 - 1



