BRADLEY OMNIDECK LAVATORY DECKS AND FAUCETS

Bradley's OmniDeck lavatory decks provide innovative solutions to sustainability, user comfort, sanitation, and site labor cost savings for contemporary washroom lavatory design.  Formed with premium recycled content materials, OmniDecks are ergonomically designed for ease of use, easy to clean and maintain, and are equipped with single-point water supply and waste hookups in a factory assembled unit.
Bradley Corporation, the industry's leading manufacturer of premium quality commercial lavatories and wash stations, presents lavatory decks made from Terreon, Bradley's premium solid surface material. Terreon solid surface material is noted for its resistance to chemicals, stains, burns and impacts. Surface damage can be easily repaired with everyday cleansers or fine grit abrasives.  Bradley's unique TerreonRE incorporates recycled content in solid surface material.

Bradley Corporation serves a diverse customer base ranging from local business facilities to international corporations like Wal-Mart, General Motors, U.S. Postal Service, W.W. Grainger, and AMC Theaters Corporation.

Architects, engineers, and specifiers look to Bradley Corporation for innovation in design and leadership in the development of environmentally conscious products.  Bradley Corporation, a member of the U.S. Green Building Council, the Wisconsin Green Building Alliance, has several products earning certification by GREENGUARD Environmental Institute, and GREENGUARD Children and Schools program.

Bradley eases the specifying process with a seasoned customer service staff and a range of helpful information tools on an advanced website.  For example, easy-to-use sizing software, available on Bradley's website, allows engineers to quickly determine the correct size Thermostatic Mixing Valves. 

Bradley is the industry leader in the manufacture of premium quality commercial plumbing fixtures, valves, TMVs and washroom accessories that appear in the following CSI MasterFormat 2004™ Sections:
Section 10 21 13 – TOILET COMPARTMENTS (Mills® Metal, Plastic-laminate, Phenolic, and Plastic units)

Section 10 28 13.13 – COMMERCIAL TOILET ACCESSORIES (Institutional and commercial accessories)

Section 10 28 13.19 – HEALTHCARE TOILET ACCESSORIES (Patient care accessories)

Section 10 28 13.21 – WARM AIR DRYERS (Aerix® hand dryers)

Section 10 28 13.63 – DETENTION TOILET ACCESSORIES 

Section 10 28 16 – BATH ACCESSORIES (Hospitality and commercial bath accessories)

Section 10 51 26 – PLASTIC LOCKERS (Lenox® Plastic Lockers)

Section 22 11 19 – DOMESTIC WATER PIPING SPECIALTIES (Thermostatic mixing valves)

Section 22 42 16.01 – COMMERCIAL LAVATORIES AND FAUCETS (Express® and Frequency® Single and multi-station lavatories)

Section 22 42 16.02 – COMMERCIAL LAVATORIES AND FAUCETS (Advocate® lavatories)

Section 22 42 16.03 – COMMERCIAL LAVATORIES AND FAUCETS (Verge™ lavatories)

Section 22 42 16.04 – COMMERCIAL LAVATORIES AND FAUCETS (OmniDecks™ lavatories)

Section 22 42 16.11 – COMMERCIAL SINKS AND FAUCETS

Section 22 42 23 – COMMERCIAL SHOWERS AND SHOWER VALVES

Section 22 42 33 – WASHFOUNTAINS (Sentry™, BradMate™, and Classic wash fountains)

Section 22 43 00 – HEALTHCARE PLUMBING FIXTURES (Patient care lavatory units)

Section 22 45 00 – EMERGENCY PLUMBING FIXTURES (Halo™ Emergency eyewash fixtures and showers)

Section 22 46 00 – SECURITY PLUMBING FIXTURES

Contact Bradley Corporation, Menomonee Falls, WI 53051; Phone: 800-BRADLEY ((800)272-3539) Fax:  (262)251-5817, or visit the Bradley web site www.bradleycorp.com.

Bradley Corporation is an AIA/CES registered provider currently offering five programs earning one (1) HS&W Learning Unit each; several qualify for sustainable design (SD) credit.  All active AIA members must successfully complete 18 learning unit (LU) hours each year.
GREENGUARD Certification ProgramSM is a service mark of GREENGUARD Environmental Institute.

Mills(, Aerix(, Lenox(, Evero(, Express(, Frequency(, Adovate(, Verge( and WashBar( are registered trademarks of Bradley Corporation.

Omni Deck™, Sentry™, Bradmate™ and Halo™ are trademarks of Bradley Corporation.

SECTION 22 42 16.04
LAVATORY DECKS AND FAUCETS
PART 1 -  GENERAL

1.1 SECTION INCLUDES

A. Solid surface material commercial lavatory units.

Specifier:  Edit below to suit Project.

B. Lavatory faucets.

C. Soap dispensers.

1.2 RELATED SECTIONS

Specifier:  Delete any paragraphs below that do not apply to this project.

Specifier: Bradley 10 28 13.13 – Commercial Toilet Accessories (Verge).

A. Division 10 Section “Toilet, Bath and Laundry Accessories” for matching design soap dispensers.

1.3 RELATED SECTIONS

Specifier:  Delete any paragraphs below that do not apply to this project.

Specifier: Bradley 10 28 13.13 – Commercial Toilet Accessories (Verge).

A. Division 10 Section “Toilet, Bath and Laundry Accessories” for matching design soap dispensers.

Specifier: Bradley 22 42 39 – Commercial Soap Dispensers and Faucets (Verge).
B. Division 22 Section "Domestic Water Piping Specialties" for thermostatic mixing valves.

Specifier: Bradley 22 42 16.01 – Commercial Lavatories and Faucets (Express Terreon solid surface)

Specifier: Bradley 22 42 16.03 – Commercial Lavatories and Faucets (Evero engineered natural quartz)

C. Division 22 Section “Commercial Lavatories and Faucets” for quartz and solid surface wash basins.

D. Division 22 Section "Commercial Lavatories and Faucets" for single- and multiple- station lavatory systems.

E. Division 22 Section "Commercial Lavatories" for commercial lavatory units with modular integrated accessories.

F. Division 22 Section "Commercial Lavatory Decks and Faucets" for single- and multiple- station lavatory decks.

Specifier: Bradley Section 22 43 00 - Healthcare Plumbing Fixtures (Patient care lavatory units)

G. Division 22 Section "Healthcare Plumbing Fixtures" for healthcare lavatories.

Specifier: Bradley Section 22 45 00 - Emergency Plumbing Fixtures (Halo Emergency eyewash fixtures and showers)

H. Division 22 Section "Emergency Plumbing Fixtures" for emergency fixtures.

Specifier: Bradley Section 22 46 00 - Security Plumbing Fixtures
I. Division 22 Section "Security Plumbing Fixtures" for security lavatories.

1.4 REFERENCES:

Specifier:  If retaining References Article in Project specification, edit below to correspond to references that remain in Section after editing.

A. American Society of Sanitary Engineering (ASSE):

1. ASSE 1070 - Water Temperature Limiting Devices.

B. American Society of Mechanical Engineers (ASME):

1. ASME A112.18.1 Plumbing Supply Fittings.

C. ASTM International (ASTM):

1. ASTM C 170 - Standard Test Method for Compressive Strength of Dimension Stone.

2. ASTM D 570 - Standard Test Method for Water Absorption of Plastics.

3. ASTM D 785 - Standard Test Method for Rockwell Hardness of Plastics and Electrical Insulating Materials.

4. ASTM D 790 - Standard Test Methods for Flexural Properties of Unreinforced and Reinforced Plastics and Electrical Insulating Materials.

5. ASTM E 84 - Standard Test Method for Surface Burning Characteristics of Building Materials.

D. Canadian Standards Association (CSA):

1. CSA B125 - (See ASME A112.18.1 - Plumbing Fixture Fittings).

Specifier:  GREENGUARD Environment Institute is an ANSI Authorized Standards Developer that oversees the GREENGUARD certification program.  GEI establishes acceptable indoor air standards for indoor products, environments, and buildings.

E. GREENGUARD Environmental Institute (GEI):

1. GREENGUARD listed and certified low emitting products.

F. International Association of Plumbing and Mechanical Officials (IAPMO):

1. Universal Plumbing Code (cUPC both U.S. and Canada).

G. International Code Council (ICC):

1. ICC/ANSI A117.1 – Accessible and Usable Buildings and Facilities.

H. National Fire Protection Association (NFPA):

1. NFPA 70 – National Electrical Code.

I. State of Texas:

1. Texas Accessibility Standards (TAS).

J. Underwriters Laboratories, Inc. (UL):

1. UL 723 - Test For Surface Burning Characteristics of Building Materials.

2. UL 1951 - Electric Plumbing Accessories.

K. United States Green Building Council (USGBC):

1. LEED Green Building Rating System (LEED).

L. US Federal Government:

1. Public Law 102-486 - Energy Policy Act. 1992 (EPACT). 

2. U.S. Architectural & Transportation Barriers Compliance Board. Americans with Disabilities Act (ADA), Accessibility Guidelines for Buildings and Facilities (ADAAG).
1.5 ACTION SUBMITTALS

A. Product Data:  For each product:

1. Manufacturer's data sheets indicating operating characteristics, materials and finishes.

2. Include details of electrical and mechanical operating parts.

3. Provide mounting requirements and rough-in dimensions.

4. Mark each sheet with product drawing designation.

B. Product Test Reports:  Indicating compliance of products with requirements, from a qualified independent testing agency, when requested by Architect.

C. Shop Drawings:  Prepared by manufacturer. Include mounting and rough-in requirements and power, signal, and control wiring diagrams. Include details of electrical and mechanical operating parts. 

Specifier:  Retain and edit below as required for LEED-registered products.  Coordinate with Division 01 requirements for LEED MR Credit 5 Regional Materials and other credits where applicable.

1.6 LEED Submittals:

Specifier:  LEED WE Credit 2 is for 50 percent reduction in water use for building sewer, based on use of water-conserving fixtures documented under Credit WE 3.  LEED WE Credit 3 is for 30, 35, or 40 percent reduction in water usage. 

1. Product Data for [Credit WE 2][and ][Credit WE 3]:  Documentation indicating compliance with requirements.
Specifier:  Bradley's TerreonRe optional solid surface material contains 25 percent preconsumer recycled content. 

2. Product data for Credit MR 4:  Indicate percentages by weight of postconsumer and preconsumer recycled content, and product cost.

1.7 INFORMATION SUBMITTALS

A. Sample warranty.

B. Manufacturer's Certificates.

C. Indoor environmental quality certificates.

1.8 MAINTENANCE SUBMITTALS

A. Furnish indicated spare parts that are packaged with identifying labels listing associated products.

B. Operation, care and cleaning instructions.

1.9 QUALITY ASSURANCE

A. Manufacturer Qualifications:  Approved manufacturer listed in this section, with minimum [5] years experience in the manufacture of plumbing fixtures. Manufacturers seeking approval must submit the following:

1. Product data, including test data from qualified independent testing agency indicating compliance with requirements.

2. Samples of each component of product specified.

3. List of successful installations of similar products available for evaluation by Architect.

4. Submit substitution request not less than 15 days prior to bid date.

B. Source Limitations:  Obtain each type of plumbing fixture and compatible accessories through one source from a single approved manufacturer.

Specifier: As of January 4, 2014, the Safe Drinking Water Act (SDWA) requires drinking water products sold or installed for use in public water systems, as well as plumbing in facilities, to meet a weighted average of not more than 0.25 percent lead.

C. Laminar-Flow, Faucet-Spout Outlets:

1. NSF Standard: Comply with NSF 372 for faucet-spout outlet materials that will be in contact with potable water.

2. Product shall meet a weighted average of not more than 0.25 percent lead as required by the U.S. Safe Drinking Water Act.

3. Description: Chrome-plated-brass, faucet-spout outlet that produces non-aerating, laminar stream. Include external or internal thread that mates with faucet outlet for attachment to faucets where indicated and flow-rate range that includes flow of faucet.

Specifier: Bradley offers handicapped-accessible fixtures meeting requirements of ADA, ICC A117.1, and Texas Accessibility Standards.

D. Accessibility Requirements: Comply with requirements of ADA \ ANSI 117.1 and with requirements of authorities having jurisdiction.

1. 306 Knee and Toe Clearance. 

2. 308 Reach Range. 

3. 606.5 Exposed Pipes & Surfaces with access panels. 

Specifier: These ADA \ ANSI 117.1 citations are valid when Bradley lavatory systems use Bradley Faucet and soap systems. Delete if not required.

4. 309.4 Operation. 

5. 606.4 Faucets.

E. Water Flow and Consumption Requirements:  Comply with EPACT.

F. Drinking Water Standard:  Comply with NSF/ANSI 372.

G. Electrical Components:  Listed and labeled per NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction.

H. Comply with Public Law 102-486, Energy Policy Act.

Specifier:  Bradley's OmniDeck lavatory decks exceed LEED for Schools IEQ requirements as certified by GREENGUARD.
I. Indoor Environmental Quality Certification:  Provide certificate indicated that lavatory deck materials have been certified under the following programs, or a comparable certification acceptable to Owner:

1. GREENGUARD Indoor Air Quality Certified.

2. GREENGUARD Certified for Children and Schools.

1.10 COORDINATION

A. Field Measurements:  Verify locations of lavatory decks and adjacent walls prior to fabrication.
1.11 WARRANTY

A. Special Manufacturer’s Warranty:  Provide manufacturer's standard form in which manufacturer agrees to repair or replace commercial lavatory decks that fail in materials or workmanship.

1. Solid surface material:  10 years.

2. Faucets:  1 year.
3. Soap Dispenser: Three years.

4. Faucets: Three years.

5. WashBar: 1 year (applies to Models LD-5010, LD-3010-WB-TR1 only)

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. Basis-of-Design Product:  Subject to compliance with requirements, provide commercial lavatory decks and faucets manufactured by Bradley Corporation, Menomonee Falls, WI 53051, (800)272-3539, fax (262)251-5817; Email info@BradleyCorp.com;  Website www.bradleycorp.com.

Specifier:  Retain one of three paragraphs below based upon Project requirements.  The manufacturer is not aware of comparable products.
1. Submit comparable products of one of the following for approval by Architect:

a. [Specifier:  Insert name of manufacturer of comparable product.]
2. Submit requests for substitution in accordance with Instructions to Bidders and Division 01 General Requirements.

3. Provide specified product; Owner will not consider substitution requests.

2.2 MATERIALS

Specifier:  Below describes Terreon, Bradley's premium densified solid surface vandal-resistant material, noted for its resistance to chemicals, stains, burns and impacts. Surface damage can be easily repaired with everyday cleansers or fine grit abrasives. Bradley’s extensive Terreon color collection allows for versatility in design options. Option in first paragraph below describes Bradley's unique optional TerreonRE which incorporates recycled content in solid surface material. TerreonRE is available in a variety of colors.
A. Solid Surface Material:  Where indicated as constructed of solid surface material, fabricate plumbing fixtures from thermoset modified bio-based resin certified by approved independent testing agency as complying with the requirements of CSA B45.5/IAPMO Z124, [with minimum 25 percent preconsumer recycled content and ]with the following minimum properties:

1. Basis of Design Product:  Bradley, [Terreon][TerreonRE].

2. Thickness:  1/2 inch (13 mm), minimum.

2.3 LAVATORY DECKS, SINGLE STATION
Specifier: Bradley OmniDeck Model LD-3010-1 Single-User Decks described below are constructed of Terreon premium solid surface material. The deck accepts individual wash station faucets and soap dispensers, and optional WashBar WDB1 Duo. Optional access panel concealing supply connections and trap.

A. ADA/ABA Compliant Wall-Mounted, Single-Station Lavatory Fixture [LAV#___]:  With integral bowl, water overflow and ledged back, drain, strainer, and tailpiece.

Specifier:  Retain Terreon OmniDeck model option below.

1. Basis of Design Manufacturer/Model:  Bradley, OmniDeck Model LD-3010-1 Terreon.

Specifier:  Select applicable material, deck edge treatment, and mounting options in subparagraphs below.

2. Material:  Solid surface material.

3. Deck Edge Accessories:  [Solid surface integral coved backsplash][Side splashes][Front apron][Side aprons].

4. Deck Nosing:  [3/8 inch (9.5 mm) radiused][Eased].
Specifier:  HS-Series and SL-Series bowls receive stainless steel access panel only. Delete option not required.

5. Access Panel:  [Stainless steel][None].

Specifier:  WB-TR1-Series bowls with the following options. Delete options not required.

6. Access Panel:  [Swing down.][Swing down w/ enclosed bottom.][Swing down matte black powder coated stainless steel.][Swing down matte black powder coated stainless steel with enclosed bottom.][None].

7. Mounting:  [Stainless steel mounting brackets][In-wall carriers specified in another section][Wall cleats specified in another section][Casework specified in another section].

8. Overall Unit Size:  30 by 22 inches (762 by 559 mm).

9. Deck Colors: As selected by Architect from manufacturer's full line.

Specifier:  Edit lavatory bowl options below to fit project. Integral bowl is available with solid surface decks; bottom mount bowl is also available with solid surface decks.
10. Integral Molded Lavatory Bowl for Solid Surface Decks:
a. Bowl Material and Size: [HS-TO1 solid surface material, oval 22 by 14 inches (558 by 355 mm)][HS-TS1 solid surface material, square, 14 by 14 inches (355 by 355 mm)][HS-TR1 solid surface material, rectangular, 22 by 16 inches (558 by 406 mm)][SL-TO1 solid surface material, oval, 16 by 13 inches (406 by 330 mm)][SL-TR1 solid surface material, rectangular, 17 by 14 inch (432 by 356 mm)][WB-TR1 solid surface material, rectangular, 21-5/8 by 11-1/2 inches (575 by 292 mm)].

b. Color:  As selected by Architect from manufacturer's full line of solid surface colors.

Specifier:  Insert WashBar WBD1; coordinate with WashBar Article below. Delete if not required.
11. WashBar:  [Insert WashBar type].
Specifier:  Insert faucet type; coordinate with Faucet Article below. Delete if not required.
12. Faucet:  [Insert faucet type].
Specifier:  Insert faucet type; coordinate with Faucet Article below. Delete if not required.
13. Soap Dispenser:  [Insert dispenser type].
14. Water Supply:  [Single tempered line][Thermostatic mixing valve assembly], with single point rough-in for unit.

15. Waste Hookup:  Single point rough-in for unit.

Specifier: Bradley OmniDeck with WashBar Model LD-5010-1 Single-User Decks described below are constructed of Terreon premium solid surface material. The deck accepts all-in-one chrome-plated stainless steel WashBar. Optional swing-down, stainless steel access panels available to conceal trap and included supply connections.
B. ADA/ABA Compliant Wall-Mounted, Single-Station Lavatory Fixture [LAV#___]:  ledged back, integral angled bowl and stainless steel drain cap to conceal trench drain. Basin and drain designed to work in harmony with WashBar technology to evacuate water and dissipate airflow to prevent splashing on the user or floor. Unit includes waste and assembly connections to wall with stops and heavy gauge stainless steel mounting brackets.
Specifier:  Retain Terreon OmniDeck model option below.

1. Basis of Design Manufacturer/Model:  Bradley, OmniDeck Model LD-5010-1 Terreon.

Specifier:  Select applicable material, deck edge treatment, and mounting options in subparagraphs below.

2. Material:  [Solid surface material].

3. Deck Edge Accessories:  [Solid surface integral coved backsplash][Side splashes][Front apron][Side aprons].

4. Deck Nosing:  [3/8 inch (9.5 mm) radiused][Eased].
Specifier:  WB-TR1-Series bowls with the following options. Delete options not required.

5. Access Panel:  [Swing down.][Swing down w/ enclosed bottom.][Swing down matte black powder coated stainless steel.][Swing down matte black powder coated stainless steel with enclosed bottom.][None].

6. Mounting:  [Stainless steel mounting brackets][In-wall carriers specified in another section][Wall cleats specified in another section][Casework specified in another section].

7. Overall Unit Size:  30 by 20-1/2 inches (762 by 521 mm).

8. Deck Colors: As selected by Architect from manufacturer's full line.
Specifier:  Edit lavatory bowl options below to fit project. Integral bowl is available with solid surface decks.

9. Integral Molded Lavatory Bowl for Solid Surface Decks:
a. Bowl Material and Size: WB-TR1 solid surface material, rectangular, 21-5/8 by 11-1/2 inches (575 by 292 mm).
b. Color:  As selected by Architect from manufacturer's full line of solid surface colors.

Specifier:  Insert WashBar WB1 or WB2 type; coordinate with WashBar Article below. Delete if not required.
10. WashBar:  [Insert WashBar type].
11. Water Supply:  [Single tempered line][Thermostatic mixing valve assembly], with single point rough-in for unit.

12. Waste Hookup:  Single point rough-in for unit.

2.4 LAVATORY DECKS, MULTIPLE STATION
Specifier: Bradley OmniDeck LD-3010 multiple-user decks described below are constructed of Terreon premium solid surface material. Bowls are positioned 30 inches on center handling washroom traffic quickly and economically while providing each user with their own space.  The deck accepts individual wash station faucets and soap dispensers, optional WashBar WBD1 Duo is available as option. Deck extensions with or without waste receptacles are optional on several units.
Bradley multi-user decks are supported by optional stainless steel brackets. Optional access panel conceals the P-trap and tailpiece, flexible stainless steel supply connections, optional Bradley thermostatic mixing valve with integral strainers and external checkstops, and optional transformers for infrared sensor control.
A. ADA/ABA Compliant Wall-Mounted, Multiple-Station Lavatory Fixture [LAV#___]:  With integral bowls, drain, strainer, and tailpiece.

Specifier:  Retain Terreon OmniDeck model below.

1. Basis of Design Manufacturer/Model:  Bradley, OmniDeck Model LD-3010 Terreon.

Specifier:  Select applicable material, configuration, deck edge treatment, and mounting options in subparagraphs below. 
2. Material:  Solid surface material.

3. Configuration:  [1][2][3][4] station deck[, with extended deck as indicated].

4. Deck Edge Accessories:  [Solid surface integral coved backsplash][Side splashes][Front apron][Side aprons].

5. Deck Nosing:  [3/8 inch (9.5 mm) radiused][Eased].

Specifier:  HS-Series and SL-Series bowls receive stainless steel access panel only. Delete option not required.

6. Access Panel:  [Stainless steel][None].

Specifier:  WB-TR1-Series bowls with the following options. Delete options not required.

7. Access Panel:  [Swing down.][Swing down w/ enclosed bottom.][Swing down matte black powder coated stainless steel.][Swing down matte black powder coated stainless steel with enclosed bottom.][None].

8. Mounting:  [Stainless steel mounting brackets][In-wall carriers specified in another section][Wall cleats specified in another section][Casework specified in another section].

Specifier:  All Bradley 3010 decks are made to order.  Deck dimensions below are typical, but lengths may be edited to fit opening. Deck depths are available between 22 and 25 inches in 1/4 inch increments.  Edit below to fit project conditions.
9. Overall Unit Size:  [60 by 24 inches (1524 by 610 mm) with 2 bowls][90 by 24 inches (2286 by 610 mm) with 3 bowls][120 by 24 inches (3048 by 610 mm) with 4 bowls][As indicated].

10. Deck Colors: As selected by Architect from manufacturer's full line.

Specifier:  Edit lavatory bowl options below to fit project. Integral bowl is available with solid surface decks; bottom mount bowl is also available with solid surface.
11. Integral Molded Lavatory Bowl for Solid Surface Decks: 
a. Bowl Material and Size: [HS-TO1 solid surface material, oval 22 by 14 inches (558 by 355 mm)][HS-TS1 solid surface material, square, 14 by 14 inches (355 by 355 mm)][HS-TR1 solid surface material, rectangular, 22 by 16 inches (558 by 406 mm)][SL-TO1 solid surface material, oval, 16 by 13 inches (406 by 330 mm)][SL-TR1 solid surface material, rectangular, 17 by 14 inches (432 by 356 mm)][WB-TR1 solid surface material, rectangular, 21-5/8 by 11-1/2 inches (575 by 292 mm)].
b. Color:  As selected by Architect from manufacturer's full line of solid surface colors.

Specifier:  Insert WashBar type; coordinate with WashBar Article below. Delete if not required.
12. WashBar:  [Insert WashBar type].
Specifier:  Insert faucet type; coordinate with Faucet Article below. Delete if not required.
13. Faucet:  [Insert faucet type].
Specifier:  Insert soap type; coordinate with soap Article below. Delete if not required.
14. Soap Dispenser:  [Insert dispenser type].
15. Water Supply:  [Single tempered line][Thermostatic mixing valve assembly], with single point rough-in for unit.

16. Waste Hookup:  Single point rough-in for unit.

Specifier: Bradley OmniDeck with WashBar LD-5010 multiple-user decks described below are constructed of Terreon premium solid surface material. The decks accepts all-in-one chrome-plated stainless steel WashBar, and individual faucet and soap dispenser. Bowls are positioned 30 inches on center handling washroom traffic quickly and economically while providing each user with their own space. Optional swing-down, stainless steel access panels available to conceal trap and included supply connections.
B. ADA/ABA Compliant Wall-Mounted, Multiple-Station Lavatory Fixture [LAV#___]:  With ledged back, integral angled bowls and stainless steel drain caps to conceal trench drains. Basin and drain designed to work in harmony with WashBar technology to evacuate water and dissipate airflow to prevent splashing on the user or floor. Unit includes individual waste and assembly connections to wall with stops and heavy gauge stainless steel mounting brackets.

Specifier:  Retain Terreon OmniDeck model below.

1. Basis of Design Manufacturer/Model:  Bradley, OmniDeck Model LD-5010 Terreon.

Specifier:  Select applicable material, configuration, deck edge treatment, and mounting options in subparagraphs below. 

2. Material:  Solid surface material.

3. Configuration:  [1][2][3][4] station deck.

4. Deck Edge Accessories:  [Solid surface integral coved backsplash][Side splashes][Front apron][Side aprons].

5. Deck Nosing:  [3/8 inch (9.5 mm) radiused roundover][Eased].

Specifier:  WB-TR1-Series bowls with the following options. Delete options not required.

6. Access Panel:  [Swing down.][Swing down w/ enclosed bottom.][Swing down matte black powder coated stainless steel.][Swing down matte black powder coated stainless steel with enclosed bottom.][None].

7. Mounting:  [Stainless steel mounting brackets][In-wall carriers specified in another section][Wall cleats specified in another section][Casework specified in another section].

Specifier:  All Bradley 5010 decks are made to order.  Deck dimensions below are typical, but lengths may be edited to fit opening. Deck depths are available between 20-1/2 and 24 inches in 1/2 inch increments.  Edit below to fit project conditions.

8. Overall Unit Size:  [30 by 20-1/2 inches (762 by 521 mm) with 1 bowl][60 by 20-1/2 inches (1524 by 521 mm) with 2 bowls][90 by 20-1/2 inches (2286 by 521 mm) with 3 bowls][120 by 20-1/2 inches (3048 by 521 mm) with 4 bowls][As indicated].

9. Deck Colors: As selected by Architect from manufacturer's full line.

Specifier:  Edit lavatory bowl options below to fit project. Integral bowl is available with solid surface decks.

10. Integral Molded Lavatory Bowl for Solid Surface Decks: 
a. Bowl Material and Size: WB-TR1 solid surface material, rectangular, with stainless steel drain cap, 21-5/8 by 11-1/2 inches (575 by 292 mm). 
b. Color:  As selected by Architect from manufacturer's full line of solid surface colors.

Specifier:  Insert WashBar WB1 All-In-One or WB2 type; coordinate with WashBar Article below. Delete if not required.
11. WashBar:  [Insert WashBar type].
12. Water Supply:  [Single tempered line] [Thermostatic mixing valve assembly], with single point rough-in for unit.

2.5 SENSOR-OPERATED WASHBAR

Specifier:  Retain descriptions of required WashBar WB1; if more than one WashBar is required, insert WashBar designation in paragraph below and use WashBar designation in Lavatory Deck Article above. 
The WashBar WB1 and WB2 All-In-One listed below are available for the OmniDeck with WashBar LD-5010 only. Delete if not required.

This plumbing fixture is designed for hand washing only. It is not Intended to dispense water for human consumption for drinking or for preparation of food or beverages.

Please visit https://www.bradleycorp.com/maintenance/soap-dispensers for soap recommendations.

A. Sleek single Casting WashBar with integral soap, faucet and single nozzle hand dryer with heated air and adjustable speeds, infrared control, smart technology with adjustable LED lighting and easy to identify icons and external tempering control FCT#___:
1. Basis of Design Manufacturer/Model:  Bradley WB1.

2. Function: Blue LED lights help guide the user, indicating the functions. The LED light will change from blue to green to signify that the function is in use. Each function is easily identified by the corresponding icon on the WashBar top surface. Each sensor includes a turn-off delay of 1-2 seconds to aid in a smooth, controlled hand-washing

3. Body:  Polished chrome plated stainless steel. Load tested to 500 pounds, WashBar is secured to the basin with two anti-rotational shanks.

Specifier: Select either chrome finish or PVD finish. Delete chrome finish if not required.

4. Chrome Finish: “PC” Polished Chrome.

Specifier: Physical Vapor Deposition is an intricate, environmentally friendly finishing process that molecularly bonds the finish to the faucet, creating a very hard, durable surface that will not corrode, discolor, or tarnish. Delete PVD finishes if not required.

5. Physical Vapor Deposition (PVD) Finish: “BB” Brushed Black Stainless.

6. Physical Vapor Deposition (PVD) Finish: “BS” Brushed Stainless.

7. Physical Vapor Deposition (PVD) Finish: “BZ” Brushed Bronze.

8. Physical Vapor Deposition (PVD) Finish: “BR” Brushed Brass.

9. Physical Vapor Deposition (PVD) Finish: “BN” Brushed Nickel.

10. Tempered Water Supply:  [Single tempered line][Single thermostatic mixing valve].

11. Flow Control: [0.35 gpm (1.33 Lpm) PCA Silicone Tip, Non-Aerated.][0.50 gpm (1.9 Lpm) PCA Silicone Tip, Non-Aerated.][None.] 

12. Soap Type: [Foam Soap Dispenser][Liquid Soap Dispenser]. Soap system accommodates up to a 1 gallon container.

13. Hand Dryer: DC Motor 120v/60hz, 20 Amp.

14. Sensor Module:  Water-conserving, durable sensor unit with adjustable timing turn-off delay and stationary object automatic timed cutoff, with diagnostic signal light.

a. Sensing Distance:  5 inches (127mm).

15. Power Supply:  120V 2A 12V DC adapter that plugs directly into the electrical outlet.

Specifier:  Retain thermostatic mixing valve if required for Project.

16. Thermostatic Mixing Valve:  Thermostatic mixing valve, ASSE 1070 listed, with stop/strainer/check valves, and flexible stainless steel connectors.

Specifier:  Retain descriptions of required WashBar WBD1; if more than one WashBar is required, insert WashBar designation in paragraph below and use WashBar designation in Lavatory Deck Article above. 
The WashBar WBD1 Duo is available with the OmniDeck LD-3010 only. Delete if not required.

Please visit https://www.bradleycorp.com/maintenance/soap-dispensers for soap recommendations.

B. Sleek single Casting WashBar with integral soap and faucet, infrared control, smart technology with adjustable LED lighting and easy to identify icons and external tempering control FCT#___:
1. Basis of Design Manufacturer/Model:  Bradley WBD1.

2. Function: Blue LED lights help guide the user, indicating the functions. The LED light will change from blue to green to signify that the function is in use. Each function is easily identified by the corresponding icon on the WashBar top surface. Each sensor includes a turn-off delay of 1-2 seconds to aid in a smooth, controlled hand-washing

3. Body:  Polished chrome plated stainless steel. Load tested to 500 pounds, WashBar is secured to the basin with two anti-rotational shanks.

Specifier: Select either chrome finish or PVD finish. Delete chrome finish if not required.

4. Chrome Finish: “PC” Polished Chrome.

Specifier: Physical Vapor Deposition is an intricate, environmentally friendly finishing process that molecularly bonds the finish to the faucet, creating a very hard, durable surface that will not corrode, discolor, or tarnish. Delete PVD finishes if not required.

5. Physical Vapor Deposition (PVD) Finish: “BB” Brushed Black Stainless.

6. Physical Vapor Deposition (PVD) Finish: “BS” Brushed Stainless.

7. Physical Vapor Deposition (PVD) Finish: “BZ” Brushed Bronze.

8. Physical Vapor Deposition (PVD) Finish: “BR” Brushed Brass.

9. Physical Vapor Deposition (PVD) Finish: “BN” Brushed Nickel.

10. Tempered Water Supply:  [Single tempered line][Single thermostatic mixing valve].

11. Flow Control: [0.35 gpm (1.33 Lpm) PCA Rubber Tip Aerator.][0.50 gpm (1.9 Lpm) PCA Rubber Tip Aerator.][None.] 

12. Soap Type: [Foam Soap Dispenser][Liquid Soap Dispenser]. Soap system accommodates up to a 1 gallon container.

13. Sensor Module:  Water-conserving, durable sensor unit with adjustable timing turn-off delay and stationary object automatic timed cutoff, with diagnostic signal light.

a. Sensing Distance:  5 inches (127mm).

14. Power Supply:  120V 2A 12V DC adapter that plugs directly into the electrical outlet.

Specifier:  Retain thermostatic mixing valve if required for Project.

15. Thermostatic Mixing Valve:  Thermostatic mixing valve, ASSE 1070 listed, with stop/strainer/check valves, and flexible stainless steel connectors.

Specifier:  Retain descriptions of required WashBar WB2; if more than one WashBar is required, insert WashBar designation in paragraph below and use WashBar designation in Lavatory Deck Article above. 
The WashBar WB2 All-In-One listed below is available for the OmniDeck with WashBar LD-5010 only. Delete if not required.

This plumbing fixture is designed for hand washing only. It is not intended to dispense water for human consumption for drinking or for preparation of food or beverages.

Please visit https://www.bradleycorp.com/maintenance/soap-dispensers for soap recommendations.

C. Sleek single Casting WashBar with integral soap, faucet and single nozzle hand dryer with heated air and adjustable speeds, infrared control, smart technology with adjustable LED lighting and easy to identify icons and external tempering control FCT#___:
1. Basis of Design Manufacturer/Model:  Bradley WB2.

2. Function: Blue LED lights help guide the user, indicating the functions. The LED light will change from blue to green to signify that the function is in use. Each function is easily identified by the corresponding icon on the WashBar top surface. Each sensor includes a turn-off delay of 1-2 seconds to aid in a smooth, controlled hand-washing

3. Body:  Polished chrome plated stainless steel. Load tested to 500 pounds, WashBar is secured to the basin with one anti-rotational shank.

Specifier: Select either chrome finish or PVD finish. Delete chrome finish if not required.

4. Chrome Finish: “PC” Polished Chrome.

Specifier: Physical Vapor Deposition is an intricate, environmentally friendly finishing process that molecularly bonds the finish to the faucet, creating a very hard, durable surface that will not corrode, discolor, or tarnish. Delete PVD finishes if not required.

5. Physical Vapor Deposition (PVD) Finish: “BB” Brushed Black Stainless.

6. Physical Vapor Deposition (PVD) Finish: “BS” Brushed Stainless.

7. Physical Vapor Deposition (PVD) Finish: “BZ” Brushed Bronze.

8. Physical Vapor Deposition (PVD) Finish: “BR” Brushed Brass.

9. Physical Vapor Deposition (PVD) Finish: “BN” Brushed Nickel.

10. Tempered Water Supply:  [Single tempered line][Single thermostatic mixing valve].

11. Flow Control: [0.35 gpm (1.33 Lpm) PCA Rubber Tip Aerator.][0.50 gpm (1.9 Lpm) PCA Rubber Tip Aerator.][None.] 

12. Soap Type: [Foam Soap Dispenser][Liquid Soap Dispenser]. Soap system accommodates up to a 1 gallon container.

13. Hand Dryer: DC Motor 120v/60hz, 20 Amp.

14. Sensor Module:  Water-conserving, durable sensor unit with adjustable timing turn-off delay and stationary object automatic timed cutoff, with diagnostic signal light.

a. Sensing Distance:  5 inches (127mm).

15. Power Supply:  120V 2A 12V DC adapter that plugs directly into the electrical outlet.

Specifier:  Retain thermostatic mixing valve if required for Project.

16. Thermostatic Mixing Valve:  Thermostatic mixing valve, ASSE 1070 listed, with stop/strainer/check valves, and flexible stainless steel connectors.

Specifier: This article specified touch-free faucets that are style matched with soap dispensers from several design series. Coordination is needed with section 10 28 00 - Toilet, Bath and Laundry Accessories and/or section 22 42 39 - Commercial Soap Dispensers and Faucets where commodity soap dispensers are typically specified. Cross reference is required in section 10 28 00 and/or 22 42 39 when style matched faucets are specified in this section. Delete article if faucets are specified in 22 42 39.
2.6 MATCHED FAUCETS

Specifier: Retain descriptions of required faucets; if more than one faucet is required, insert faucet designation in paragraph below and use faucet designation in Lavatory Deck Article above. Delete if not required.
A. Deck Mounted Faucet – General:

1. Basis of Design Manufacturer/Model: Bradley Verge 
2. Touch free dual sensor activation.

3. Compliance and Certifications: 

a. ADA ANSI/ICC A117.1, Citation 609.3.

b. ASME A112.18.1/CSA B125.1.

c. NSF/ANSI 372 – Lead Free.

d. NSF/ANSI 61.

e. cUPC.

f. CE electrical components.

4. Vandal-resistant construction shall include concealed sensor package, durable finish, and anti-rotational gasket/washer.

5. In-line filter supplied with either mixing assembly or tempered line assembly to trap debris.

6. Operation: Dual sensors utilizing time of flight and diffuse reflective sensors.

a. Operating Water Pressure Range: 20 to 125 psi.

b. Faucet activates water flow only when user’s hands enter the infrared detection zone.

c. Faucet turns off after user’s hands are removed from the lavatory bowl area.

d. Eleven (11) second run time (with or without hands under sensor). Manually set run time using control module (4s, 11s, 15s, 30s, 60s, 180s with or without auto system rinse).

e. Sixty (60) second auto system rinse every 24 hours. Option for sanitary manual flush.

Specifier: Select either chrome finish or PVD finish. Delete chrome finish if not required.

7. Chrome Finish: “PC” Polished Chrome.

Specifier: Physical Vapor Deposition is an intricate, environmentally friendly finishing process that molecularly bonds the finish to the faucet, creating a very hard, durable surface that will not corrode, discolor, or tarnish. Delete PVD finishes if not required.

8. Physical Vapor Deposition (PVD) Finish: “BB” Brushed Black Stainless.

9. Physical Vapor Deposition (PVD) Finish: “BS” Brushed Stainless.

10. Physical Vapor Deposition (PVD) Finish: “BZ” Brushed Bronze.

11. Physical Vapor Deposition (PVD) Finish: “BR” Brushed Brass.

12. Physical Vapor Deposition (PVD) Finish: “BN” Brushed Nickel.

Specifier: Refined high arc design pairs with soap model 6-3100 and integrates seamlessly with Bradley lavatories. Touch-free, dual-sensor activation with time of flight and diffuse reflective sensors that work in tandem to detect and confirm the user's presence, eliminating false activations. Battery pack standard or optional AC adapter with battery back-up. Faucet shall feature chrome-plated cast brass construction with optional in-stock PVD finish. Low-flow laminar device options available to conserve water. Vandal-resistant construction includes concealed sensor package, vandal-resistant laminar flow device, durable PVD finish options, and anti‑rotational locking nut. Delete if not required.

B. Electronic Lavatory Faucets:

1. Sensor-Operated, High-Arc Profile Metering Faucet with Infrared Control FCT#___: Vandal- resistant accessible faucet meeting ASME A112.18.1/CSA B125. ADA/ANSI A117.1 compliant.

a. Basis of Design Manufacturer/Model: Bradley Verge, Crestt Series, Model S53-3100.

b. Body:  Commercial solid cast brass.

c. Water Supply: [Tempered Line Assembly (Supply Hose and Shut-Off Included)][Navigator Thermostatic Mixing Assembly (Supply Hose and Shut-Off Included)].

d. Flow Type: [0.35 gpm (1.3 Lpm) Silicone Tip, multiple individual laminar flow streams][0.5 gpm (1.9 Lpm) Silicone Tip, multiple individual laminar flow streams].

Specifier: Delete if not required.

e. Drain Strainer: Finish to match.

f. Sensor Module: Water-conserving, vandal-resistant dual sensors utilizing time of flight and diffuse reflective sensors with timing turn-off delay and stationary object automatic timed cutoff.
Specifier: Delete power supply not required.

g. Power Supply: Battery (standard).

h. Power Supply: 120VAC/6VDC, 50/60Hz plug-in transformer adapter with battery back-up. 4x AA batteries (included). Low battery indicator on spout. 

Specifier: Splitter kit powers up to four faucets or combination of four faucets and soap dispensers.

i. Power Supply: Provide power supply “splitter’ for 2, 3 or 4 faucets as required. Provide 14 feet (4.3 m) extension power cable as required.

Specifier: Refined, cylindrical design pairs with soap model 6-3300 and integrates seamlessly with Bradley lavatories. Touch-free, dual-sensor activation with time of flight and diffuse reflective sensors that work in tandem to detect and confirm the user's presence, eliminating false activations. Battery pack standard or optional AC adapter with battery back-up. Faucet shall feature chrome-plated cast brass construction with optional in-stock PVD finish. Low-flow laminar device options available to conserve water. Vandal-resistant construction includes concealed sensor package, vandal-resistant laminar flow device, durable PVD finish options, and anti‑rotational locking nut. Delete if not required.

C. Electronic Lavatory Faucets:

1. Sensor-Operated, Tubular Design Metering Faucet with Infrared Control FCT#___: Vandal- resistant accessible faucet meeting ASME A112.18.1/CSA B125. ADA/ANSI A117.1 compliant.

a. Basis of Design Manufacturer/Model: Bradley Verge, Metro Series, Model S53-3300.

b. Body:  Commercial solid cast brass.

c. Water Supply: [Tempered Line Assembly (Supply Hose and Shut-Off Included)][ Navigator Thermostatic Mixing Assembly (Supply Hose and Shut-Off Included)].

d. Flow Type: [0.35 gpm (1.3 Lpm) Silicone Tip, multiple individual laminar flow streams][0.5 gpm (1.9 Lpm) Silicone Tip, multiple individual laminar flow streams].

Specifier: Delete if not required.

e. Drain Strainer: Finish to match.

f. Sensor Module: Water-conserving, vandal-resistant dual sensors utilizing time of flight and diffuse reflective sensors with timing turn-off delay and stationary object automatic timed cutoff.

Specifier: Delete power supply not required.

g. Power Supply: Battery (standard). 

h. Power Supply: 120VAC/6VDC, 50/60Hz plug-in transformer adapter with battery back-up. 4x AA batteries (included). Low battery indicator on spout.  

Specifier: Splitter kit powers up to four faucets or combination of four faucets and soap dispensers.

i. Power Supply: Provide power supply “splitter’ for 2, 3 or 4 faucets as required. Provide 14 feet (4.3 m) extension power cable as required.

Specifier: Sleek lines and curved-edge design pairs with soap model 6-3500 and integrates seamlessly with Bradley lavatories. Touch-free, dual-sensor activation with time of flight and diffuse reflective sensors that work in tandem to detect and confirm the user's presence, eliminating false activations. Battery pack standard or optional AC adapter with battery back-up. Faucet shall feature chrome-plated cast brass construction with optional in-stock PVD finish. Low-flow laminar device options available to conserve water. Vandal-resistant construction includes concealed sensor package, vandal-resistant laminar flow device, durable PVD finish options, and anti‑rotational locking nut. Delete if not required.

D. Electronic Lavatory Faucets:

1. Sensor-Operated, Tubular Design Metering Faucet with Infrared Control FCT#___: Vandal- resistant accessible faucet meeting ASME A112.18.1/CSA B125. ADA/ANSI A117.1 compliant.

a. Basis of Design Manufacturer/Model: Bradley Verge, Linea Series, Model S53-3500.

b. Body:  Commercial solid cast brass.

c. Water Supply: [Tempered Line Assembly (Supply Hose and Shut-Off Included)][ Navigator Thermostatic Mixing Assembly (Supply Hose and Shut-Off Included)].

d. Flow Type: [0.35 gpm (1.3 Lpm) Silicone Tip, multiple individual laminar flow streams][0.5 gpm (1.9 Lpm) Silicone Tip, multiple individual laminar flow streams].

Specifier: Delete if not required.

e. Drain Strainer: Finish to match.

f. Sensor Module: Water-conserving, vandal-resistant dual sensors utilizing time of flight and diffuse reflective sensors with timing turn-off delay and stationary object automatic timed cutoff.

Specifier: Delete power supply not required.

g. Power Supply: Battery (standard). 

h. Power Supply: 120VAC/6VDC, 50/60Hz plug-in transformer adapter with battery back-up. 4x AA batteries (included). Low battery indicator on spout.  

Specifier: Splitter kit powers up to four faucets or combination of four faucets and soap dispensers.

i. Power Supply: Provide power supply “splitter’ for 2, 3 or 4 faucets as required. Provide 14 feet (4.3 m) extension power cable as required.

Specifier: Sleek design pairs with soap model 6-3700 and integrates seamlessly with Bradley lavatories. Touch-free, dual-sensor activation with time of flight and diffuse reflective sensors that work in tandem to detect and confirm the user's presence, eliminating false activations. Battery pack standard or optional AC adapter with battery back-up. Faucet shall feature chrome-plated cast brass construction with optional in-stock PVD finish. Low-flow laminar device options available to conserve water. Vandal-resistant construction includes concealed sensor package, vandal-resistant laminar flow device, durable PVD finish options, and anti‑rotational locking nut. Delete if not required.

E. Electronic Lavatory Faucets:

1. Sensor-Operated, Tubular Design Metering Faucet with Infrared Control FCT#___: Vandal- resistant accessible faucet meeting ASME A112.18.1/CSA B125. ADA/ANSI A117.1 compliant.

a. Basis of Design Manufacturer/Model: Bradley Verge, Zen Series, Model S53-3700.

b. Body:  Commercial solid cast brass.

c. Water Supply: [Tempered Line Assembly (Supply Hose and Shut-Off Included)][ Navigator Thermostatic Mixing Assembly (Supply Hose and Shut-Off Included)].

d. Flow Type: [0.35 gpm (1.3 Lpm) Silicone Tip, multiple individual laminar flow streams][0.5 gpm (1.9 Lpm) Silicone Tip, multiple individual laminar flow streams].

Specifier: Delete if not required.

e. Drain Strainer: Finish to match.

f. Sensor Module: Water-conserving, vandal-resistant dual sensors utilizing time of flight and diffuse reflective sensors with timing turn-off delay and stationary object automatic timed cutoff.

Specifier: Delete power supply not required.

g. Power Supply: Battery (standard). 

h. Power Supply: 120VAC/6VDC, 50/60Hz plug-in transformer adapter with battery back-up. 4x AA batteries (included). Low battery indicator on spout.
Specifier: Splitter kit powers up to four faucets or combination of four faucets and soap dispensers.

i. Power Supply: Provide power supply “splitter’ for 2, 3 or 4 faucets as required. Provide 14 feet (4.3 m) extension power cable as required.

Specifier: This article specified touch-free soap dispensers that are style matched with faucets from several design series. Coordination is needed with section 10 28 00 - Toilet, Bath and Laundry Accessories and/or section 22 42 39 - Commercial Soap Dispensers and Faucets where commodity soap dispensers are typically specified. Cross reference is required in section 10 28 00 and/or 22 42 39 when soap dispensers are specified in this section. Delete article if soap dispensers are specified in 10 28 00 or 22 42 39.
Specifier: Delete soap dispensers if not required.

2.7 MATCHED SOAP DISPENSERS

A. Deck Mounted Soap Dispensers – General:

1. Touch free infrared sensor-operated.

2. Multi-station system shall supply up to six soap dispensers.

3. Compliance and Certifications: 

a. ADA / ICC ANSI A117.1, Citation 609.4.

b. UL electrical components.

c. CE electrical components.

4. Vandal-resistant construction shall include concealed sensor package, durable finish, and anti-rotational gasket/washer.

Specifier: Select either chrome finish or PVD finish. Delete chrome finish if not required.

5. Chrome Finish: “PC” Polished Chrome.

Specifier: Physical Vapor Deposition is an intricate, environmentally friendly finishing process that molecularly bonds the finish to the faucet, creating a very hard, durable surface that will not corrode, discolor, or tarnish. Delete PVD finishes if not required.

6. Physical Vapor Deposition (PVD) Finish: “BB” Brushed Black Stainless.

7. Physical Vapor Deposition (PVD) Finish: “BS” Brushed Stainless.

8. Physical Vapor Deposition (PVD) Finish: “BZ” Brushed Bronze.

9. Physical Vapor Deposition (PVD) Finish: “BR” Brushed Brass.

10. Physical Vapor Deposition (PVD) Finish: “BN” Brushed Nickel.

Specifier: Refined high arc design pairs with faucet model S53-3100 and integrates seamlessly with Bradley lavatories. The dispenser is available with an individual or multi-feed top-fill tank that is compatible with bulk foam or liquid soap. The multi-feed station system supplies soap to up to 6 soap dispensers. Activation through a touch-free infrared sensor that pairs seamlessly with Bradley's faucet dual sensor technology to eliminate false activations and maximize battery life. Dispenser shall feature chrome-plated cast brass construction with optional in-stock PVD finish. Vandal‑resistant construction includes concealed sensor package, durable PVD finish options, and anti-rotational gasket/washer.  Delete if not required.

B. Sensored Soap Dispenser SD#__: Deck-mounted, sensor-operated, cast brass, with LED battery and soap level indicators, [with battery box and batteries. 70.5 oz (2080 mL) capacity bottle.][with single dispenser 120VAC powerpack. 70.5 oz (2080 mL) capacity bottle.][with maximum of 6 dispenser 120VAC powerpack. Multi-feed Tank: 166.5 oz (5026 ml).]
1. Basis of Design Manufacturer/Model: Bradley Verge Deck-Mounted Soap Dispenser, Crestt Series, Model 6-3100. 

Specifier: Refined, cylindrical design pairs with faucet model S53-3300 and integrates seamlessly with Bradley lavatories. The dispenser is available with an individual or multi-feed top-fill tank that is compatible with bulk foam or liquid soap. The multi-feed station system supplies soap to up to 6 soap dispensers. Activation through a touch-free infrared sensor that pairs seamlessly with Bradley's faucet dual sensor technology to eliminate false activations and maximize battery life. Dispenser shall feature chrome-plated cast brass construction with optional in-stock PVD finish. Vandal‑resistant construction includes concealed sensor package, durable PVD finish options, and anti-rotational gasket/washer. Delete if not required.

C. Sensored Soap Dispenser SD#__: Deck-mounted, sensor-operated, cast brass, with LED battery and soap level indicators, [with battery box and batteries. 70.5 oz (2080 mL) capacity bottle.][with single dispenser 120VAC powerpack. 70.5 oz (2080 mL) capacity bottle.][with maximum of 6 dispenser 120VAC powerpack. Multi-feed Tank: 166.5 oz (5026 ml).]
1. Basis of Design Manufacturer/Model: Bradley Verge Deck-Mounted Soap Dispenser, Metro Series, Model 6-3300. 

Specifier: Sleek lines and curved edges design pairs with faucet model S53-3500 and integrates seamlessly with Bradley lavatories. The dispenser is available with an individual or multi-feed top-fill tank that is compatible with bulk foam or liquid soap. The multi-feed station system supplies soap to up to 6 soap dispensers. Activation through a touch-free infrared sensor that pairs seamlessly with Bradley's faucet dual sensor technology to eliminate false activations and maximize battery life. Dispenser shall feature chrome-plated cast brass construction with optional in-stock PVD finish. Vandal‑resistant construction includes concealed sensor package, durable PVD finish options, and anti-rotational gasket/washer. Delete if not required.

D. Sensored Soap Dispenser SD#__: Deck-mounted, sensor-operated, cast brass, with LED battery and soap level indicators, [with battery box and batteries. 70.5 oz (2080 mL) capacity bottle.][with single dispenser 120VAC powerpack. 70.5 oz (2080 mL) capacity bottle.][with maximum of 6 dispenser 120VAC powerpack. Multi-feed Tank: 166.5 oz (5026 ml).]
1. Basis of Design Manufacturer/Model: Bradley Verge Deck-mounted Soap Dispenser, Linea Series, Model 6-3500. 

Specifier: Sleek design pairs with faucet model S53-3700 and integrates seamlessly with Bradley lavatories. The dispenser is available with an individual or multi-feed top-fill tank that is compatible with bulk foam or liquid soap. The multi-feed station system supplies soap to up to 6 soap dispensers. Activation through a touch-free infrared sensor that pairs seamlessly with Bradley's faucet dual sensor technology to eliminate false activations and maximize battery life. Dispenser shall feature chrome-plated cast brass construction with optional in-stock PVD finish. Vandal‑resistant construction includes concealed sensor package, durable PVD finish options, and anti-rotational gasket/washer. Delete if not required.

E. Sensored Soap Dispenser SD#__: Deck-mounted, sensor-operated, cast bronze, with LED battery and soap level indicators, [with battery box and batteries. 70.5 oz (2080 mL) capacity bottle.][with single dispenser 120VAC powerpack. 70.5 oz (2080 mL) capacity bottle.][with maximum of 6 dispenser 120VAC powerpack. Multi-feed Tank: 166.5 oz (5026 ml).]
1. Basis of Design Manufacturer/Model: Bradley Verge Deck-Mounted Soap Dispenser, Zen Series, Model 6-3700. 

Specifier: Delete if not required.

2.8 SENSORED SOAP DISPENSER

A. Deck-mounted, sensor-operated SD#__: Chrome-plated plastic, with LED battery and soap level indicators, [with battery box and batteries][with single dispenser 120VAC powerpack][with 4 dispenser 120VAC powerpack], [27 oz (798 mL) capacity bottle][1000 shot soap].
1. Basis of Design Manufacturer/Model: Bradley, Model 6315-KT0000.

Specifier: Delete if not required.

1. MANUAL SOAP DISPENSER

B. Deck-mounted SD#__: [16 oz. (473 mL) plastic][32 oz. (946 mL) plastic] globe, with 4 inch (102 mm) spout.

1. Basis of Design Manufacturer/Model: Bradley, Model 6324.

C. Deck-mounted SD#__: 16 oz. (473 mL) plastic globe, with 3-1/2 inches (88.90 mm) spout.

1. Basis of Design Manufacturer/Model: Bradley, Model 6334. 

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine conditions and verify opening measurements prior to commencing installation.  Proceed with installation once conditions meet requirements.
3.2 INSTALLATION

A. Assemble fixtures and associated fittings and trim in accordance with manufacturer's instructions.

B. At time of Substantial Completion:
1. Clean unit surfaces per manufacturer’s care instructions, test fixtures and leave in ready-to-use condition.

2. Install new batteries in battery operated devices.

3. Fill soap dispensers.

4. Turn over keys, tools, maintenance instructions and maintenance stock to Owner.
C. Install Single-Point Connections:  

1. Install water supply piping to unit. Provide stop on each supply in readily-serviced location. Fasten supply piping to supports or substrate.

2. Install trap and waste piping to unit.

D. Install escutcheons at exposed piping penetrations in finished locations and within cabinets.

E. Seal joints between fixtures and walls, floors, and countertops with joint sealant specified in Division 07 Section "Joint Sealants."
Specifier: Delete soap dispenser mounting requirements if not included in this section.

F. Mount soap dispenser in 1-3/8 inches (35 mm) diameter hole in lavatory or countertop 1-1/2 inches (38 mm) from edge of sink. Shank will accommodate a maximum counter thickness of 1-1/2 inches (38 mm).

3.3 CLEANING AND PROTECTION

A. Repair or replace defective work, including damaged fixtures and components.

B. Clean unit surfaces, test fixtures, and leave in ready-to-use condition.

C. Install new batteries in battery-operated devices at time of Substantial Completion. 

D. Turn over keys, tools, maintenance instructions, and maintenance stock to Owner.

E. Protect units with water-resistant temporary covering. Do not allow temporary use of plumbing fixtures unless approved in writing by Architect. Remove protection at Substantial Completion and dispose.

3.4 TESTING AND ADJUSTING

A. Set field-adjustable temperature set points of temperature-actuated water mixing valves.  Adjust set point within allowable temperature range.

B. Test and adjust installation.

C. Remove and replace malfunctioning thermostatic mixing valves and retest.

END OF SECTION
BRADLEY CORPORATION
22 42 16
LAVATORY DECKS AND FAUCETS

<Page 1 of 19>



