- Section 095100 
USG ALTATM Data Center STRUCTURAL Grid & Acoustical Ceilings - USG

PART 1  GENERAL

SECTION INCLUDES

Suspended Extruded Heavy Duty Load-Bearing Grid Ceiling Systems.

Acoustical Ceiling Panels.

- The paragraph below is optional text

Supplementary acoustical insulation above ceiling.

Wall angles and shadow moldings.

- The paragraph below is optional text

Special trims and accessories.

RELATED REQUIREMENTS

Section 016116 - Volatile Organic Compound (VOC) Content Restrictions.

REFERENCE STANDARDS

ASTM A580/A580M - Standard Specification for Stainless Steel Wire; 2018.

ASTM A653/A653M - Standard Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process; 2020.

ASTM B209/B209M - Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate; 2021a.

ASTM C423 - Standard Test Method for Sound Absorption and Sound Absorption Coefficients by the Reverberation Room Method; 2022.

ASTM C635/C635M - Standard Specification for Manufacture, Performance, and Testing of Metal Suspension Systems for Acoustical Tile and Lay-in Panel Ceilings; 2022.

ASTM C636/C636M - Standard Practice for Installation of Metal Ceiling Suspension Systems for Acoustical Tile and Lay-In Panels; 2019.

ASTM E84 - Standard Test Method for Surface Burning Characteristics of Building Materials; 2022.

ASTM E119 - Standard Test Methods for Fire Tests of Building Construction and Materials; 2020.

- The paragraph below is optional text

ASTM E413 - Classification for Rating Sound Insulation; 2022.

ASTM E1264 - Standard Classification for Acoustical Ceiling Products; 2022.

UL (GGG) - GREENGUARD Gold Certified Products; Current Edition.

ADMINISTRATIVE REQUIREMENTS

Coordination: Coordinate work of this section with installation of mechanical and electrical components and with other construction activities affected by work of this section.

Review with affected installers those locations of facility services lines and equipment within ceiling plenum that prevent installation of hangers at spacings compliant with limitations established in referenced standards. Arrange for each affected mechanical or electrical installer to provide necessary number of additional structural support points for ceiling installer.

Preinstallation Meeting: Convene one week before starting work of this section.

Sequencing: Schedule work of affected trades to minimize or eliminate installation conflicts and rework.

Supply hanger clips during steel deck erection. Supply additional hangers and inserts as required.

Ensure that acoustical ceilings are not installed until building is enclosed, sufficient heat is provided, dust generating activities have terminated, and overhead work is completed, tested, and approved. Do not install acoustical units until after interior wet work is dry.

SUBMITTALS

See Section 013000 - Administrative Requirements for submittal procedures.

Shop Drawings: Indicate grid layout and related dimensioning.

Product Data: Provide data on suspension system components and acoustical units.

Samples: Two samples [_____] by [_____] inches ([_____] by [_____] mm) in size indicating material and finish of acoustical units.

Samples: Two samples each, [____] inches ([____] mm) long of suspension system main runner, cross runner, and perimeter molding.

- The paragraph below is optional text

Manufacturer's Installation Instructions: Indicate special procedures and perimeter conditions requiring special attention.

Designer's Qualification Statement.

Installer's Qualification Statement.

Maintenance Materials: Furnish the following for Owner's use in maintenance of project.

- The paragraph below is optional text

See Section 016000 - Product Requirements for additional provisions.

- The paragraph below is optional text

Extra Acoustical Units: [____] sq ft ([____] sq m) of each type and size.

- The paragraph below is optional text

Extra Acoustical Units: Quantity equal to 5 percent of total installed.

QUALITY ASSURANCE

Single Source Responsibility: Provide structural grid, required hanger spacing and associated ceiling tile and accessories by a single manufacturer.

Shop Drawings: Provide engineered grid drawings, details and layouts of design elements that require coordination with the design-build team.

Product Data: Submit the following manufacturers:

Product data

Installation guides

Specifications

Design details

Technical product data

Structural Calculations: Provide specific documentation and calculations by a licensed Professional Structural Engineer that is accredited in the state or local municipality that the project is located in. Consultant shall furnish local project requirements including, but not limited to Structural loading, Seismic design, wind loading and Structural Grid deal load requirements.

Designer Qualifications for Seismic Design: Perform under direct supervision of a Professional Structural Engineer experienced in design of this work and licensed in the State in which the Project is located.

Installer Qualifications: Contractor specializing in performing work of the specified type and with at least three years of documented experience and approved by manufacturer.

FIELD CONDITIONS

Maintain uniform temperature of minimum 60 degrees F (16 degrees C), and maximum humidity of 40 percent before, during, and after acoustical unit installation.

PART 2  PRODUCTS

CEILING ASSEMBLIES

Acoustical Ceiling Assembly Type [APC-1]:

Acoustical Units: [MarsTM 1"] [MarsTM 3/4"].

Nominal Panel Size: [24 inches by 24 inches (2’ by 2’) panel (609.6 mm by 609.6 mm)], [24 inches by 48 inches (2’ by 4’) panel (609.6 mm by 1219.2 mm)].

Panel Edge: SQ edge.

Color: Flat White 050.

Characteristics: Noise Reduction Coefficient = [0.75], [0.90], Ceiling Attenuation Class = [30], [35], Light Reflectance = 0.90, Recycled Content = [71%], [73%], Environmental Product Declaration: Yes, Health Product Declaration: Yes, GreenGuard Gold: Yes, EC3 Score: N/A, ClimaPlus Warranty: Yes.

Suspension Grid: USG ALTATM Structural Suspension System.

Color: Mill Finish Aluminum.

Acoustical Ceiling Assembly Type [APC-2]:

Acoustical Units: [HalcyonTM (Foil Backed) 1"], [HalcyonTM 1"], [HalcyonTM 3/4"], [Halcyon TM Eco 1"].

Nominal Panel Size: [24 inches by 24 inches (2’ by 2’) panel (609.6 mm by 609.6 mm)], [24 inches by 48 inches (2’ by 4’) panel (609.6 mm by 1219.2 mm].

Panel Edge: SQ edge.

Color: [Flat White 050], [custom color].

Characteristics: Noise Reduction Coefficient = [0.9],[0.95], Ceiling Attenuation Class = [20], [27], Light Reflectance = [0.90], Recycled Content = [37%], [38%], [40%], Environmental Product Declaration: Yes, Health Product Declaration: Yes, GreenGuard Gold: Yes, EC3 Score: N/A, ClimaPlus Warranty: Yes.

Suspension Grid: USG ALTATM Structural Suspension System.

Color: Mill Finish Aluminum.

Acoustical Ceiling Assembly Type APC-3:

Acoustical Units: [USG Sheetrock® Brand 1/2"], [Sheetrock® Brand Clean Room 1/2"].

Panel Size: [24 inches by 24 inches (2’ by 2’) panel (609.6 mm by 1219.2 mm)], [24 inches by 48 inches (2’ by 4’) panel (609.6 mm by 1219.2 mm)].

Panel Edge: SQ edge.

Color: [Flat White 050].

Characteristics: Noise Reduction Coefficient = [N/A], Ceiling Attenuation Class = [35] [40], Light Reflectance = [0.77], Recycled Content = [8%], Environmental Product Declaration: [N/A], Health Product Declaration: [N/A], GreenGuard Gold: [Yes], EC3 Score: [N/A], ClimaPlus Warranty: [N/A].

Suspension Grid: USG ALTATM Structural Suspension System.

Color: Mill Finish Aluminum.

Ceiling PERFORMANCE REQUIREMENTS

USG ALTATM Extruded Data Center Ceiling Grid has the following load requirements:

Maximum safe working uniform load – This value is the max area per hanger divided into the max load safe capacity of the Threaded Rods and Turnbuckles is 1,200 lbs.

Point load at L/360 – Deflection limit is 0.133” @ L=48” and 0.20” @ L=72”.

Allowable point load – Recommended max load with a factor of safety of 1.67 applied from material yield.

Point load at yield – Predicted load, in lbs., when material starts to yield and further deformation will be no longer elastic.

Allowable load assumes point loads spaced min 4ft centers on section suspended between hangers on a 4’ x 4’ installation or 6ft centers on a 4’ x 6’ system.

Maximum static point load at turnbuckle, 1,200 lbs. or 75 lbs./sq. ft. for a 4’ x 4’ system.

A factor of safety of 1.67 is applied to the load at yield.

Seismic Performance: Ceiling systems designed to withstand the effects of earthquake motions determined according to ASCE 7 for Seismic Design Category [D],[E],[or F] and complying with the following:

- The paragraph below is optional text

Local authorities having jurisdiction.

- The paragraph below is optional text

ICC-ES Evaluation Report No. [__________].

Ceiling COMPONENT PRODUCTS

Acoustical Units:

Acoustical Units - General: ASTM E1264, Fire Class A.

VOC Content: As specified in Section 016116.

VOC Content: Certified as Low Emission by one of the following:

Product listing in UL (GGG).

Product listing in CHPS (HPPD).

Noise Reduction Coefficient (NRC) rating, Ceiling Attenuation Class (CAC) rating, and Light Reflectance Coefficient (LR) performance for each type of unit specified below, as determined in accordance with ASTM E1264.

Fire Class / Surface Burning Characteristics: Determined in accordance with test method ASTM E84.

Surface Burning Characteristics: Unless otherwise indicated, flame spread index of [25 or less], smoke developed index of [50 or less].

Acoustical Panels: Mineral fiber with membrane-faced overlay, with the following characteristics:

Classification: ASTM E1264-23 Type A, Form A2.1, Pattern E & G.

Form(s): Includes the following, as applicable to each product specified.

Form 1 - Nodular.

Form 2 - Water felted.

Pattern(s): Includes the following, as applicable to each product specified.

E - Lightly textured.

G - Smooth.

Thickness: As applicable to each product specified.

Recycled Content: As applicable to selected products.

Material Ingredients Transparency: Products included in the USG EcoBlueprint Program.

Low Emissions (VOC): Greenguard-certified products.

Products:

USG Corporation; MarsTM 3/4" Panels.

USG Corporation; MarsTM 1” Panels.

Substitutions: [Not permitted].

Acoustical Panels: Glass fiber with membrane-faced overlay, with the following characteristics:

Classification: ASTM E1264-23 Type B, Form B2, Pattern E & G.

Form(s): Includes the following, as applicable to each product specified.

Form 2 - Cloth.

Pattern(s): Includes the following, as applicable to each product specified.

E - Lightly textured.

G - Smooth.

Thickness: As applicable to each product specified.

Recycled Content: As applicable to selected products.

Material Ingredients Transparency: Products included in the USG EcoBlueprint Program.

Low Emissions (VOC): Greenguard-certified products.

Products:

USG Corporation; HalcyonTM 3/4" Panels.

USG Corporation; Halcyon TM 1" Panels.

USG Corporation; Halcyon TM Eco 1" Panels.

USG Corporation; Halcyon TM (Foil Backed) 1" Panels.

Substitutions: Not permitted.

Acoustical Panels: Gypsum, with the following characteristics:

Classification: ASTM E1264-23 Type G, Form G2, Pattern G.

Pattern(s): Includes the following, as applicable to each product specified.

G - Smooth.

Thickness: As applicable to each product specified.

Recycled Content: As applicable to selected products.

Material Ingredients Transparency: Products included in the USG EcoBlueprint Program.

Low Emissions (VOC): Greenguard-certified products.

Products:

USG Corporation; Sheetrock® Brand Clean Room 1/2" Panels.

Substitutions: Not permitted.

Suspension Systems:

Extruded Aluminum Heavy Duty Suspension Systems - General: Complying with ASTM C635; [standard length] [field cut] and interlocking components, with [Suspension Hubs],[splices],[wall angles and moldings] as required.

Materials:

Extruded 6005 T5 Aluminum Grid: ASTM C635, clear anodized, unless otherwise indicated.

Structural Classification: Heavy-duty load-bearing, when tested in accordance with ASTM C635.

Recycled Materials Content: Classified as containing greater than 50 percent total recycled content. Available for specific sizes and lengths.

Profile: Tee; 2 1/2” x 2” (63.5 x 51 mm).

Finish: Anodized Aluminum.

Color: Clear.

Products:

USG Corporation; USG ALTATM Structural Suspension System:

Main Tee: SGX40 (12’-0”) [3658 mm].

Cross Tee: SGX440 (4’-0”) [610 mm].

Cross Tee: SGX240 (2’-0”) [305 mm].

Perimeter Tee: SGXWM40 (12’-0”) [3658 mm].

Substitutions: Not permitted.

Moldings and Trim:

Perimeter Wall Moldings: [Same metal and finish as grid].

Size: As required for installation conditions [None - N/A].

Angle Moldings: Asymmetrical L-shaped, for mounting at same elevation as face of grid.

ACCESSORIES

Intersection Brackets and Main Tee Splices: Zinc Die Cast Hubs.

4-Way Intersection Bracket: SGXIB4W

3-Way Intersection Bracket: SGXIB3W

Corner Intersection Bracket: SGXIBC

In-Line Main Tee Splice Hanger Support: SGXSHS

Hub Bolts to Lock Hubs to USG ALTATM Main, Cross, and Perimeter Tees: SGXACB

Suspension Rod-Turnbuckle: 3/8” galvanized threaded rod with lock nut to engage and lock to intersection brackets, with included turnbuckle (3/8” – 16 right hand). Contractor to coordinate rod size, threading, and thread pitch to suspend ceiling up to structure past top edge of turnbuckle.

- The paragraph below is optional text

Compression Framing and Bracing: Metal stud sizes, gauges, and spacings as determined by qualified structural design professional and complying with applicable codes.

- The paragraph below is optional text

Compression Posts: 3.4 inch (19 mm) nominal diameter EMT conduit, lengths as required by installation conditions.

- The paragraph below is optional text

Hold-Down Clips: SGXACHC1 manufacturer's standard clips to suit application.

- The paragraph below is optional text

Seismic Clips: Manufacturer's standard clips for seismic conditions and to suit application.

- The paragraph below is optional text

Touch-Up Paint for Exposed Surfaces: Type and color to match acoustical units and suspension system grid and trim elements.

Touch-Up Paint for Concealed Items: [Zinc rich] type, as recommended by ceiling system manufacturer.

Fabrication

Shop fabricate ceiling [None - N/A] components to the greatest extent possible.

Fabricate components to allow access to ceiling plenum as required.

PART 3 EXECUTION

EXAMINATION

Verify existing conditions before starting work.

Verify that layout of hanger rods will not interfere with other work.

Verify that field measurements are as indicated on shop drawings.

Start of installation constitutes acceptance of project conditions.

Preparation

Coordinate the location of hanger rods with other work.

Provide hanger clips during steel deck erection. Provide for anticipated additional hangers and inserts as required.

Install ceiling system after major above-ceiling work is complete.

Acclimate USG MarsTM Ceiling Tiles by removing from packaging in installation area a minimum of 72 hours prior to installation.

INSTALLATION - SUSPENSION SYSTEM

Install suspension system in accordance with ASTM C636/C636M and manufacturer's instructions and as supplemented in this section.

Coordinate and verify that contractor provided rods are compatible with the SGXACLW turnbuckle prior to ordering suspension rods that attach to structure above.

Install hanger rods and coordinate with overhead work. Provide additional hanger rods and supports as required.

Rigidly secure system, including integral mechanical and electrical components, for maximum deflection of 1:360.

- The paragraph below is optional text

Lay out system to a balanced grid design with edge units no less than 50 percent of acoustical unit size.

- The paragraph below is optional text

Locate system on room axis according to reflected ceiling plan.

- The paragraph below is optional text

Seismic Suspension System, Seismic Design Category C: Hang suspension system independent of walls, columns, ducts, pipes and conduit. Maintain a 3/8 inch (9 mm) clearance between grid ends and wall.

- The paragraph below is optional text

Seismic Suspension System, Seismic Design Categories D, E, F: Hang suspension system with grid ends attached to the perimeter molding on two adjacent walls; on opposite walls, maintain a 3/4 inch (19 mm) clearance between grid ends and wall.

Where ducts, facility services, or equipment prevent the regular spacing of hangers, reinforce the nearest affected hangers and related carrying channels to span the extra distance.

Do not support components on main runners or cross runners if weight causes total dead load to exceed deflection capability.

Support fixture loads using supplementary hangers located within 6 inches (152 mm) of each corner, or support components independently.

Do not eccentrically load system or induce rotation of runners.

Edge Moldings: Install at intersection of ceiling and vertical surfaces and penetrations, using components of maximum length; set level. Provide edge moldings at junction with other ceiling finishes. Miter corners. Provide preformed edge closures to match bullnosed cornered partitions.

Install in bed of acoustical sealant.

Use longest practical lengths.

Overlap and rivet corners.

- The paragraph below is optional text

Install light fixture boxes constructed of gypsum board above light fixtures in accordance with fire rated assembly requirements and light fixture ventilation requirements.

INSTALLATION - ACOUSTICAL UNITS

Install acoustical units in accordance with manufacturer's instructions.

Fit acoustical units in place, free from damaged edges or other defects detrimental to appearance and function.

Fit edge trim neatly against abutting surfaces.

Install acoustical units level, in uniform plane, and free from twist, warp, and dents.

Cutting Acoustical Units:

Cut to fit irregular grid and perimeter edge trim.

Make field cut edges of same profile as factory edges.

Lay acoustical insulation for a distance of 48 inches (1219 mm) either side of acoustical partitions as indicated.

Install hold down clips on acoustical units within 20 ft (6 m) of an exterior door.

TOLERANCES

Maximum Variation from Flat and Level Surface: 1/8 inch in 10 feet (3 mm in 3 m).

Maximum Variation from Plumb of Grid Members Caused by Eccentric Loads: Two degrees.

Cleaning

Clean and touch up minor finish damage. Remove and replace components that cannot be successfully cleaned and repaired.

- END OF SECTION